## Sheet1
Instructions:
The intent is for this Checklist to be used during project punchlist time and all items be marked as complete prior to scheduling a Certificate of Occupancy.
This will help prevent any additional items being found during the CoO walkdown and preventing CoO signatures.
The entire IPT can use this to evaluate if they are prepared for the CoO walkdown prior to it occurring
Project PID:
Project Name:
DCF:
Responsible Engineer:
SME | POC | Status - Pending or Complete | Item | Description | Notes
Lead Inspector |  | Pending | Punchlist Completion | Punchlist is complete and all Category A items are resolved.
Lead Inspector |  | Pending | Special Inspections | All special inspections are completed and documented. | See project Statement of Special Inspections
Lead Inspector |  | Pending | Electrical Inspections | All completed final inspections. | See project Test and Inspection Plan
Lead Inspector |  | Pending | Pressure Safety Inspections | If a PSIP is required, all paperwork has been completed and accepted by LANL. | If programmatic, might be deferred to prior to equipment start-up.
Lead Inspector |  | Pending | Fire Suppression System Inspections | Flush & hydrostatic tests have been accepted and documentation completed.
Lead Inspector |  | Pending | Lightning Protection Aerials, Grounding Cables | Verify system has been inspected and accepted.
Lead Inspector |  | Pending | Lightning Protection Counterpoise | Verify system has been inspected and accepted.
Lead Inspector |  | Pending | Mechanical Systems | Backflow preventors for potable water and sanitary sewer have been tested/certified.
OSH-ISH |  | Pending | Electrical Acceptance | Permit affirming electrical system is safe to operate and can be energized. | Reference Utility Authorization for service UI-PROC-63-00-180-R4 and/or Authorization for electrical equipment/services when utility is not involved OSH-ISH-OP-022.0/Form 2.
Fire marshal |  | Pending | Fire Suppression System | Representative witnesses testing and acceptance of system. Typical documentation that may be requested includes flow test, drain test, backflow preventer functional test, labeling/tags for fire riser and PIV, and locks for fire riser. | FSR entry for valve tags, signs and locks an acceptable alternative
Fire marshal |  | Pending | Fire Suppression Contractors Material Test Certificate for Underground Pipe | Completed (no blanks, all required tests performed and documented) - if underground pipe was installed. Provided to LANL AHJ at least 1 day prior to CoO signature day for review
Fire marshal |  | Pending | Fire Suppression Contractors Material Test Certificate for Above Ground Pipe | Completed (no blanks, all required tests performed and documented) - if a sprinkler system was installed. Provided to LANL AHJ at least 1 day prior to CoO signature day for review
Fire marshal |  | Pending | Fire Alarm System | Representative witnesses testing and acceptance of system. Fire Alarm Record of Completion must be provided to LANL AHJ at least 1 day prior to CoO signature day for review. Remove construction covers on devices and appliances.
Fire marshal |  | Pending | As Built Drawings | Redline summary of any as-built changes over the approved design, Provided to LANL AHJ at least 1 day prior to CoO signature day for review
Fire marshal |  | Pending | Means of Egress | Representative verifies the following items are functional: unencumbered path of egress, tripping hazards not present, stair and ramp dimensions, door hardware correct with proper functionality, handrails, guardrails, paths to muster area.
Fire marshal |  | Pending | Emergency Lighting and EXIT signage | Provide documentation that shows emergency lighting has passed a 90 minute discharge test and lighting levels meet minimum lumens throughout the path of egress.
Fire marshal |  | Pending | Building identification (TA-BLDG) sign installed | For identification during incident response.
Fire marshal |  | Pending | E911 Address | If required by PRID (PRIDs open prior to 2-1-2020 may not have the proper E911 review, assume new occupied buildings will need an E911 address))
Fire marshal |  | Pending | Evacuation Map | Installed if required, See ESM Ch 4 and ESM Ch 16 requirements for applicability.
Fire marshal |  | Pending | Fire sprinkler system misc | Spare sprinkler cabinet, spare heads, wrench(es), sprinkler inventory, system information sign, hydraulic placard, air vent discharge, freeze protection, overspray or paint on sprinkler heads, escutcheon install
Fire marshal |  | Pending | Fire Lanes | Construction items blocking fire lane/fire lane obstructions, access to fire hydrants and FDCs
Fire marshal |  | Pending | Opening Protectives (fire doors, dampers, windows) | Verify proper ratings, operation, hardware, fusible links, and functional testing documentation (e.g., roll-up doors by manufacturer endorsed representative, fire or smoke damper operation and documetation)
Fire marshal |  | Pending | Thru-Penetration Firestop Systems and (spray-on) fireproof coatings | Verify installed assemblies with UL system and/or EJ, labeling is present and correct, inspection reports, map (if required by Spec). Fireproof coating installation inspections, patching of coating (hand application) following new attachments and hangers to steel.
Fire marshal |  | Pending | Pre incident plan walkdown requested from LAFD/ ES-FP | Notify ES-FP Tammy Dominguez to schedule PIP walkdown. Should occur after substantial construction is complete but prior to CoO or securing the building.
Fire marshal |  | Pending | Review of Construction Inspections | Construction inspection documentation for required FP inspections per ESM Chapter 2 - "Fire Protection Division of Responsibilities for Construction Inspection". Available for LANL AHJ review at least 1 day prior to CoO signature day.
Fire marshal |  | Pending | Fire Extinguishers and Signage | Installed and inspected (if fire extinguishers are required)
Fire marshal |  | Pending | Fire water run-off collection features | Verify inspection reports. Confirm testing (if required) of drainage systems.
PM/PE |  | Pending | Design Changes | All design changes (FCRs/DRNs/NCRs) that could impact 10CFR851 worker safety have been resolved.
PM/PE |  | Pending | Submittals | All submittals concerning systems with a safety function have at least a Code 2 approval level.
Design Authority |  | Pending | NCRs | All NCRs that could impact 10CFR851 worker safety have been resolved.
Commissioning Authority |  | Pending | Cx Activites | Cx Activites in regard to safety systems have been completed.
Physical Security Systems |  | Pending | Security/Safeguard Systems Operational | All security and safeguards are in compliance with Ch. 9 of the ESM. Typical issues that must be accepted are badge readers, security fencing, and manproofing.