## TIS_TIP Guidance
Workbook Purpose | This normally-optional template facilitates the development of a project's Test and Inspection Summary (TIS) to facilitate development of a T&I Plan or planning document (TIP). The Constructor is responsibile for producing the TIP in accordance with Section 01 4000 or 01 4001 (hereafter "01 4000" for simplicity) "Quality Requirements" of the Project Specifications, or when otherwise contractually mandated. The terms Test & Inspection Plan and TIP refer to any document containing the T&I planning specifics. For most projects, the “plan” must or should be integral to the project construction execution schedule (possibly filtered for the T&I tasks); however, for small projects that do not warrant a formal schedule or work breakdown structure as determined by the Integrated Project Team (IPT), issuing the plan standalone or on the drawings or sketches is more likely. The TIP must identify all applicable testing, inspection, and related quality control requirements based on LANL’s Engineering Standards Manual (ESM) Chapter 16, including but not limited to Sections IBC-GEN and IBC-IP and, where relevant, testing, inspection, and quality control requirements imposed through the design package and/or the Engineer-of-Record (EOR)–generated Statement of Special Inspections (SSI). Approaches and formats specified in LANL Master Spec 01 4000 will always contain an acceptable approach/format as they have LANL authorities (AHJs) and Chief Inspector concurrence. For small modification projects, streamlining of the necessary information is expected, and beyond that, alternative approaches/formats may be approved as a type 1 variance by the Ch. 16 POC. To support this TIP process, this workbook offers a customizable format for the design agency (EOR) preparing a TIS during the design and pre-construction phases. A TIS is often not a required document. It is a summary typically produced by the design agency (EOR) that is (1) useful for discussing intended test & inspection requirements in the specs with LANL AHJs and SMEs, and (2) is a very helpful feeder to a TIP. While this document (ESM Ch. 16 IBC-IP Att. I) is intended to provide a customizable template for preparing a TIS, the requirement for, format of, and party responsible for preparing a TIS is dependant upon the determination of the LANL IPT. The TIS is intended to be developed collaboratively by the Integrated Project Team (IPT), Design Professional in Responsible Charge (DPIRC), LANL Building Official, LANL Chief Electrical Inspector, LANL Fire Marshal, and LANL Utilities, based on which requirements apply to the project scope. The TIS is a key tool to help the Constructor interpret applicable requirements and develop a comprehensive TIP. At a minimum, the TIS should capture all quality control points that must be documented in project records to support acceptance of work. This workbook includes a tab for a TIS coversheet. ⚠️ Important: Neither a TIS nor a TIP create or eliminate testing or inspection requirements. They serve to consolidate and summarize those requirements already established by the project design, applicable codes, and invoked standards. Additional QA/QC processes may be implemented by the constructor, owner, IPT, DPIRC, LANL Building Official, LANL Chief Electrical Inspector, LANL Fire Marshal, and LANL Utilities to promote quality outcomes. These activities are discretionary based on stakeholder judgment and should be described within the Project Quality Management Plan, when present, rather than the TIS or TIP.
Workbook Layout | This is multi-tabbed Excel workbook. When using this workbook to develop a TIS, before issuance, this Pink (TIS_TIP Guidance) tab should be deleted or othersie not included and, possibly, the Green (Legend, Defn's, and WBS Example) tab shortened. Refer to the legend on the last, green tab (Legend, Definitions, and WBS Example) for abbreviations/definitions of responsible parties and tasks. The gray TIS Coversheet tab is a template that may be used by the Designer or Record to create a coversheet for the TIS, which is normally an edit of the other tabs. On the blue Spec-Based Tasks tab, the requirements from LANL's master guide specifications are summarized by spec section. The requirements are organized into three categories: 1) Inspections 2) QC Verifications 3) Testing The party responsible for the oversight or administration of each Hold Point is indicated (Owner column). The requirement basis and/or the location of the requirement in the specification is provided to allow easy reference and greater context when needed. When using this workbook to develop a TIS, be sure to update the tab based upon the project specific revision to the LMS or the project specific alternative specifications. The orange Code-Based Inspections tab summarizes inspections from the LANL Building Codes and their incorporated-by-reference standard requirements (these often span multiple spec section tasks). When using this workbook to develop a TIS it will be necessary to collaborate with the applicable LANL permitting authorities to identify which inspections are applicable to the scope of the project. It is typically beneficial to remove or gray-out/highlight inspection references that are not applicable to the scope of the project. WBS: On the green WBS (etc.) tab, a brief illustration of a deliverable-based Work Breakdown Structure (WBS) has been provided, incorporating the requirements from both the Spec-Based tab and the Code-Based tab into a WBS with high level tasks outlining the planned sequence of work and its relationship to the identified hold points. This is one example of an acceptable format for a Project TIP submittal. Other WBS types or a construction schedule may also be acceptable. Refer to the project 01 4000 specification section to determine the acceptable formats.
Workbook is Guidance | This guidance document (unedited) is not intended to serve as a project's TIS or TIP, but is a tool to help produce them. NDE (nondestructive examination) note: Projects with extensive NDE may wish to create a separate NDE TIS (NTIS) and/or TIP (NTIP) and refer out to it; ref. LANL Master Spec Section 01 4525 (r0, 1.5.A.7).
Summary of Att. I Revisions | Rev. 0: Initial issuance, 9/24/2013
Rev. 1, 3/22/2023: Complete revision and update, simplified/streamlined. Addition of code-based inspections and instructions on separate tabs. Incorporated VAR-10564 (constructor develops, not design agency). 2021 IBC, IFC, UMC, and UPC and 2020 NEC compliant.
Rev. 2, 03/25/2026: TIP Template became “Test & Inspection Summary (TIS) Template (Guidance)," implementing VAR-10761. Explanation tab became TIS_TIP Guidance to reflect changes and discuss new concepts, add quality management diagram. TIS Coversheet tab added. Created Legend, Defn's, and WBS Example tab. On Spec-Based tab, removed QC Submittals and "Witness Points." On Code-Driven tab, added pressure safety row for when ASME, IFC and NFPA tasks for the Fire Marshal's Office, and columns for discipline and inspection type. Manufacturer's tech rep presence added for selected fire (code tab) and roofing (specs). Implements commercial/conventional initiative.

## TIS Coversheet
Project Information
Project ID#
Project Title
TA-BLDG
DCF#
| DPIRC | Name
Phone
Email
Rev, Date
This document has been prepared specifically for the subject project. The following pages provide a summary of the minimum testing and inspection documentation that is required for acceptance of the project scope of work as understood by the Design Professional in Responsible Charge. This document is intended to aid the Subcontractor/Constructor in understanding the requirements conveyed in the specifications, drawings, and applicable codes and standards. Inclusion or omission from this summary document does not relieve or impose upon the Subcontractor responsibility for complying with the requirements of the Subcontract.
This document has been reviewed against the project design and scope of work as indicated below

## Spec-Based Tasks
Sort Seq | Sec Div | Discipline | Section No. | Sec Rev | Section Title | Task | Task Type | Hold or Witness Point | Owner | Requirement Reference | Spec Reference (correct as needed)
1 | 03 | Structural | 03 3001 | 19 | Reinforced Concrete | Pre-Placement Testing and Sampling (Coordinate with Code-Driven Inspections) | Testing | Hold | TA |  | 03 3001 3.11.F
2 | 03 | Structural | 03 3001 | 19 | Reinforced Concrete | Post-Placement Testing (Coordinate with Code-Driven Inspections) | Testing | Hold | TA |  | 03 3001 3.11.G
3 | 03 | Structural | 03 3053 | 11 | Miscellaneous Cast-In-Place Concrete | Pre-Placement Testing and Sampling (Coordinate with Code-Driven Inspections) | Testing | Hold | TA |  | 03 3053 3.4.C
4 | 03 | Civil | 03 3053 | 11 | Miscellaneous Cast-In-Place Concrete | Post-Placement Testing (Coordinate with Code-Driven Inspections) | Testing | Hold | TA |  | 03 3053 3.4.D
5 | 03 | Structural | 03 4100 | 3 | Precast Structural Concrete | Sand-cement and non-shrink grout compressive strength testing (Coordinate with Code-Driven Inspections) | Testing | Hold | TA |  | 03 4100 3.4.C
6 | 03 | Structural | 03 6000 | 4 | Grouting | Pre-Placement Sampling (Coordinate with Code-Driven Inspections) | Testing | Hold | TA | ACI 301 / ASME NQA-1 | 03 6000 3.4.D
7 | 03 | Structural | 03 6000 | 4 | Grouting | Post-Placement Testing (Coordinate with Code-Driven Inspections) | Testing | Hold | TA | ACI 301 / ASME NQA-1 | 03 6000 3.4.B&C
8 | 05 | Structural | 05 0520 | 6 | Post-Installed Concrete and Grouted-Masonry Anchors - Normal Confidence | Witness testing of permanent grouted anchors (Coordinate with Code-Driven Inspections) | QC Verification | Hold | OBI |  | 05 0520 3.10.B.1
9 | 05 | Structural | 05 1000 | 12 | Structural Metal Framing | QCI-Field welding, high-strength bolting (Coordinate with Code-Driven Inspections) | Testing | Hold | TA |  | 05 1000 3.5.B.1
10 | 05 | Structural | 05 1000 | 12 | Structural Metal Framing | SFRS Field/ Erector QC (Coordinate with Code-Driven Inspections) (seismic force-resisting) | Testing | Hold | TA |  | 05 1000 3.6
11 | 05 | Structural | 05 2100 | 6 | Steel Joist Framing | Visual Inspection of welds and bolted connections (Coordinate with Code-Driven Inspections) | Testing | Hold | TA | AWS D1.1 | 05 2100 3.3.B-C
12 | 07 | Architectural | 07 2400 | 4 | Exterior Insulation and Finish Systems | Testing and Inspections (Coordinate with Code-Driven Inspections) | Testing | Hold | OBI | ASTM E-2568, ICC-ES AC24, ICC-ES AC219 | 07 2400 3.8.C
13 | 07 | Architectural | 07 5213.13 | 3 | Atatic-Polypropylene Modified-Bitumen Roofing, Cold-Applied | Final Inspection by roofing system manufacturer's representative | Testing | Hold | TA | ASTM D-3617 | 07 5213.13 3.13.C
14 | 07 | Architectural | 07 5217 | 2 | Styrene-Butadiene-Styrene Modified-Bituminous Membrane Roofing, Cold-Applied | Final Inspection by roofing system manufacturer's representative | Testing | Hold | TA | ASTM D-3617 | 07 5217 3.14.C
15 | 11 | Mechanical | 11 5311.18 | 1 | Glovebox Atmosphere Regenerable Purification Systems | Power termination/installation | QC Verification | Hold | QC |  | 11 5311.18 3.1.A
16 | 11 | Mechanical | 11 5311.18 | 1 | Glovebox Atmosphere Regenerable Purification Systems | Startup - ensure the purification unit has regenerated 3x prior to bringing online | QC Verification | Hold | QC |  | 11 5311.18 3.3.A
17 | 13 | Structural | 13 3419 | 6 | Metal Building Systems | QCI Field Quality Control | Testing | Hold | TA |  | 13 3419 3.11
18 | 13 | Structural | 13 3419 | 6 | Metal Building Systems | SFRS QC (seismic force-resisting) | Testing | Hold | TA |  | 13 3419 3.12
19 | 22 | Mechanical | 22 0813 | 12 | Testing Piping Systems | Witnessing of pressure testing (Coordinate with Code-Driven Inspections) | QC Verification | Hold | OBI |  | 22 0813 1.4.A
21 | 22 | Mechanical | 22 1343.16 | 2 | Facility Wet-Well Packaged Sewage Pumping Stations (Interior) | LANL acceptance inspection LANL’s Facilities Management Representative | QC Verification | Hold | QC |  | 22 1343.16 3.4.A.-B
23 | 23 | Mechanical | 23 3225 | 3 | Bag-in Bag-out Housings | In-place testing | Testing | Hold | TA |  | 23 3225 1.2.A
24 | 26 | Electrical | 26 0519 | 8 | Low Voltage Electrical Power Conductors and Cables | Witness and document torquing on not less than 10% of each type of connector and terminal when required | QC Verification | Hold | QC |  | 26 0519 3.9.E.3
25 | 26 | Electrical | 26 0700 | 4 | Induction Motors-500HP and Smaller | Witness the torquing of accessible bolted electrical connections. | QC Verification | Hold | QC |  | 26 0813 3.4.B.1
26 | 26 | Electrical | 26 2419 | 5 | Motor Control Centers | Witness of torquing of all bus bar splices | QC Verification | Hold | QC / CEIO / Cx | *NEIS NECA 402 7.1 | 26 2419.3.5.A.2
27 | 26 | Electrical | 26 2816 | 5 | Enclosed Switches and Circuit Breakers | Witness torquing electrical terminations | QC Verification | Hold | QC / CEIO / Cx | NFPA 70 110.14.D (NEC) | 26 2816 3.5.C
28 | 26 | Electrical | 26 2913 | 4 | Enclosed Controllers | Witness of torquing power conductor terminations | QC Verification | Hold | QC / CEI / Cx | NFPA 70 110.14.D (NEC) | 26 2913.3.6.C
29 | 26 | Electrical | 26 3353 | 3 | Static Uninterruptible Power Supply | Witness proper torque of accessible bus connections and mechanical fasteners during installation of UPS | QC Verification | Hold | QC |  | 26 3353 3.6.B
30 | 26 | Electrical | 26 4100 | 5 | Facility Lightning Protection | Acceptance Inspection | Inspection | Hold | CEIO |  | 26 4100 1.2.A
31 | 31 | Civil | 31 2000 | 10 | Earth Moving | Verify fill material to be placed is within the stated specifications (Proctor)(Coordinate with Code-Driven Inspections) | Testing | Hold | TA |  | 31 2000 3.10.F.1
32 | 31 | Civil | 31 2000 | 10 | Earth Moving | Verify field moisture and density (Compaction Testing)(Coordinate with Code-Driven Inspections) | Testing | Hold | TA |  | 31 2000 3.10.F.2-4
33 | 31 | Civil | 31 2323.33 | 6 | Flowable Fill | Field Samples and Laboratory Testing | Testing | Hold | TA |  | 31 2323.33 3.5.A
34 | 31 | Civil | 31 2323.33 | 6 | Flowable Fill | Field Testing | Testing | Hold | TA |  | 31 2323.33 3.5.B
35 | 32 | Civil | 32 1216 | 6 | Asphalt Paving | Test Strip | Testing | Hold | TA |  | 3.8.A
36 | 32 | Civil | 32 1216 | 6 | Asphalt Paving | Hot Asphalt Sample | Testing | Hold | TA |  | 3.8.C
37 | 32 | Civil | 32 1216 | 6 | Asphalt Paving | Field Density Testing | Testing | Hold | TA |  | 3.8.C
38 | 32 | Civil | 32 1216 | 6 | Asphalt Paving | Asphalt Core Sample and Field Testing | Testing | Hold | TA |  | 3.8.C
39 | 32 | Civil | 32 1216 | 6 | Asphalt Paving | Laboratory Testing of Hot Asphalt Samples (Major Asphalt) | Testing | Hold | TA |  | 3.8.C.2
40 | 32 | Civil | 32 8400 | 3 | Planting Irrigation | Acceptance Inspection | QC Verification | Hold | OBI |  | 32 8400 3.7.A Rev. 4
41 | 32 | Civil/Arch | 32 9219 | 5 | Seeding | Verify 70 percent of area seeded is cover | QC Verification | Hold | OBI |  | 32 9219 3.10.A
42 | 32 | Civil/Arch | 32 9223 | 3 | Sodding | Inspection and acceptance | QC Verification | Witness | OBI |  | 32 9223 3.5.A
43 | 32 | Civil/Arch | 32 9300 | 5 | Plants | Inspection and acceptance | QC Verification | Hold | OBI |  | 32 9300 3.5
44 | 33 | Civil | 33 1000 | 9 | Water Utilities | Acceptance Inspection | Inspection | Hold | UI |  | 33 1000 3.3.A
45 | 33 | Civil | 33 3000 | 7 | Sanitary Sewerage Utilities | Acceptance Inspection | Inspection | Hold | UI |  | 33 3000 3.3.A
46 | 33 | Civil | 33 3000 | 7 | Sanitary Sewerage Utilities | Final video inspection | Inspection | Hold | UI |  | 33 3000 3.7.B
47 | 33 | Civil | 33 3200 | 7 | Wastewater Utility Pumping Stations | Acceptance inspections | Inspection | Hold | UI |  | 33 3200 3.4.A.1
48 | 33 | Civil | 33 4000 | 4 | Storm Drainage Utilities | Acceptance Inspection | Inspection | Hold | UI |  | 34 4000 3.5.C
49 | 33 | Civil | 33 5100 | 11 | Natural-Gas Distribution | Acceptance Inspection | Inspection | Hold | UI |  | 33 5100 3.8.C
50 | 33 | Civil | 33 6300 | 5 | Steam Energy Distribution | Acceptance Inspection | Inspection | Hold | UI |  | 33 6300 3.4.A
51 | 33 | Electrical | 33 7119 | 6 | Electrical Underground Ducts and Manholes | Manhole Inspection | QC Verification | Hold | QC/OBI |  | 33 7119 3.7.B Rev. 6
52 | 33 | Electrical | 33 7311 | 4 | Pad-Mounted Transformer Rough-In | Field inspections to be performed by LANL U&I | Inspection | Hold | UI |  | 33 7311 3.5
53 | 33 | Electrical | 33 7711 | 4 | Pad-Mounted Switch Rough-In | Inspections to be performed by LANL-UI | Inspection | Hold | UI |  | 33 7711 3.6.A
54 | 22 | Mechanical | 40 0504 | 2 | Process Piping | Category M Fluid Service Piping leak test (Coordinate with Code-Driven Inspections) | Testing | Hold | TA | ASME B31.3 M345 & 345.8 | 40 0504 3.3.O.9.c
55 | 41 | Mech/Structural | 41 2213.13 | 2 | Bridge Cranes | Final inspection | Inspection | Hold | OBI |  | 41 2213.13 3.7.C
56 | 41 | Mech/Structural | 41 2213.13 | 2 | Bridge Cranes | Field testing and final inspection | Testing | Hold | TA |  | 41 2213.13 3.7.B

## Code-Driven Inspections
Constructor shall notify the STR when work is ready for these Hold Point inspections and provide access to and means for inspections of such work (2021 IBC 110.5)
Discipline | Reference | Title | Inspection Type | Description | Owner | Notes
All | 2021 IBC 110.3.10 | IBC Final inspection | Final Acceptance | The final inspection shall be made after all work required by the building permit is completed. | OBI
Architectural | 2021 IBC 1705.17 | Exterior Insulation and Finish Systems (EIFS) -- Periodic Special inspection | Coordinate with Special inspector | Water-resistive barrier coating | SI | exception for those over a water-resistive barrier with a means of draining moisture to the exterior or EIFS over masonry or concrete walls
Architectural | 2021 IBC 110.3.3 | Lowest floor elevation | Prior to Concealment | In flood hazard areas, upon placement of the lowest floor, including the basement, and prior to further vertical construction, the elevation certification required in Section 1612.5 shall be submitted to the building official. | OBI | In flood hazard areas only (rare)
Architectural | 2021 IBC 110.3.7 | Weather-exposed balcony and walking surface waterproofing | Prior to Concealment | Where balconies or other elevated walking surfaces have weather-exposed surfaces, and the structural framing is protected by an impervious moisture barrier, all elements of the impervious moisture barrier system shall not be concealed until inspected and approved | OBI | Exception: Where special inspections are provided in accordance with Section 1705.1.1, Item 3
Electrical | 2021 IBC K106.3 | Electrical Rough-in inspection | Prior to Concealment | Rough-in inspection shall be made after the roof, framing, fire blocking and bracing are in place and all wiring and other components to be concealed are complete, and prior to the installation of wall or ceiling membranes. | CEIO
Electrical | 2021 IBC K106.2 | Electrical Underground inspection | Prior to Concealment | Underground inspection shall be made after trenches or ditches are excavated and bedded, piping and conductors installed, and before backfill is put in place. Where excavated soil contains rocks, broken concrete, frozen chunks, and other rubble that would damage or break the raceway, cable or conductors, or where corrosive action will occur, protection shall be provided in the form of granular or selected material, approved running boards, sleeves or other means. | CEIO
Electrical | 2021 IBC 110.3.10 | Final inspection (CEIO) | Final Acceptance | Final inspection shall be made upon completion of the installation (and to receive authorization to energize; ref. LANL P101-13 Electrical Safety [Att. A 3.4.3.B]) | CEIO
Fire Protection | 2019 NFPA 111 7.6 | Emergency and Standby Power Systems (Stored Electrical Energy) - Installation Acceptance Testing | Final Acceptance | Functional Testing, Full Load Testing, Safety Indications and Shutdowns Testing, | CX/FPO
Fire Protection | 2019 NFPA 110 7.13 | Emergency and Standby Power Systems Installation Acceptance Testing | Final Acceptance | Functional Testing, Full Load Testing, Cycle Crank Testing, Safety Indications and Shutdowns Testing | CX/FPO
Fire Protection | 2021 IFC 108.2 | Emergency Lighting Units Dependent on Integral Batteries - Testing and Commissioning | Final Acceptance | Emergency Lighting Units shall be tested to confirm illumination levels and duration satisfy per NFPA 101 | CX/FPO | ESM Ch.2 Section D4050 10.0.D
Fire Protection | 2021 IFC 108.2 | Fire Access Roadways and Fire Lane Inspection | Final Acceptance | Fire department access roadways and associated fire lane marking and signage shall be inspected according to NFPA–Fire Code and IFC criteria for fire department access roadways and FP Office requirements for fire lane marking. Inspection shall include verification of intended fencing, gates, Knox Box, fire hydrant, fire department connection (FDC) and apparatus accessibility | FPO | ESM Ch.2 Section D4050 4.0.D
Fire Protection | 2019 NFPA 72-14.4.1 | Fire Alarm System - Initial Acceptance/Reacceptance Testing | In-Process Inspection | Continuity and/or megger testing of conductors/cable. Proper functionality of fire alarm system devices. Proper functionality of fire alarm system logic and control functions including auxiliary functions per design documents. Proper remote reporting to CAS. Authorization to Energize issued | FPO/CEIO
Fire Protection | 2019 NFPA 72-14.3 | Fire Alarm System - Initial/Reacceptance Inspection | Prior to Concealment | Proper routing of FA (fire alarm) conduit, raceway, etc. Proper support of FA conduit, raceway, etc. System components are installed in proper locations and at proper heights per design documents. FA conductors/cabling installed per design documents. Proper voltage of FA conductors. Field-installed normal AC power wiring conforms to NFPA 70. Field-installed FA wiring conforms to NFPA 72 and manufacturer specs. Wiring and termination to control panels and field devices are properly routed and landed per design documents | FPO
Fire Protection | 2019 NFPA 72 7.5.6 | Fire Alarm System - Record of Completion | Approved Project Submittal | Detailing system design, installation, testing, and acceptance. This includes as-built drawings, equipment specifications, and test result | FPO | Project Specifications should include as submittal
Fire Protection | 2021 IBC 110.3.8 | Fire- and smoke-resistant penetrations - Non-SI Inspection | Prior to Concealment | Protection of joints and penetrations in fire-resistance-rated assemblies, smoke barriers and smoke partitions shall not be concealed from view until inspected and approved. | OBI | Includes fire-resistant doors (incl. access, frames, glazing, hardware), windows
Fire Protection | 2021 IFC 108.2 | Fire Code Inspection - Final | Final Acceptance | The fire code official shall conduct such inspections as deemed necessary to determine compliance with this code before work is concealed, e.g.: -Sprinkler heads are properly installed (type, orifice size, orientation, coverage, temperature rating, etc.) -Proper installation of system components (valves, alarm valves, trim, alarm devices, supervisory air, backflow prevention, drains, gauges and other appurtenances) per design documents -Fire-rated walls/barriers labeled/stenciled with appropriate rating -Fire/smoke dampers and duct smoke detectors are installed per design documents -Proper setting (fusible link temp) and operation of fire dampers -Installation/placement and appropriateness with hazards in accordance with design documents | FPO
Fire Protection | 2019 NFPA 80 19.4 | Fire Dampers Acceptance Inspection | Final Acceptance | Visual inspection and operational testing of all fire dampers. | FPO/OBI | 2021 UMC 606.2
Fire Protection | 2019 NFPA 80 5.2 | Fire Doors / Fire Windows Inspection and Operational Test | Final Acceptance | Doors/windows, frames and hardware have proper rating, properly close and latch, and are labeled per design documents. Doors/windows properly operate (release, close, latch) when inter-locked with fire detection and alarm system | FPO/OBI
Fire Protection | 2015 IFC 901.5 | Fire Protection and Life Safety Systems - Installation Acceptance Testing | In-Process Inspection | The Fire Code Official shall be notified before any required testing | FPO
Fire Protection | 2019 NFPA 20 14.1.3 | Fire Pump Certified Test Certificate | Approved Project Submittal | Documentation of commissioning results shall include a Contractor’s Material and Test Certificate for Private Fire Service Mains (suction and discharge piping to/from the fire pumps), a Contractor’s Material and Test Certificate for Fire Pump Systems (one for each pump), and a manufacturer’s certified pump test characteristic curve to validate as-installed performance. | FPO | Project Specifications should include as submittal. ESM Ch.2 Section D4050 4.0.B.1
Fire Protection | 2019 NFPA 20 14.2 | Fire Pump Field Acceptance Testing | In-Process Inspection | Flow testing of fire pump, comparison to shop curve. Proper signage, labels and flow arrows on piping and components Fire Alarm testing of system devices Sequence of operation testing of system Testing of pump engine / motor "Backflow prevention device(s) forward flow and back flow testing and certification (IAW O&M 406)" | FPO | Project Specifications should include manufacturer's field services and submittal reports. ESM Ch.2 Section D4050 4.0.B
Fire Protection | 2019 NFPA 20 14.1 | Fire Pump Hydrostatic Tests and Flushing | In-Process Inspection | Fire protection pumps and associated appurtenances (piping, valves, pressure maintenance pumps, controllers, fuel systems, battery systems, testing devices, enclosures, etc.) shall be inspected and commissioned to NFPA 20, Standard for Installation of Stationary Pumps for Fire Protection. | OBI | ESM Ch.2 Section D4050 4.0.B
Fire Protection | 2021 IFC 108.2 | Fire Pump System Rough-in Inspection | Prior to Concealment | Inspection of Fire Pump system components after installation and prior to concealment | OBI
Fire Protection | 2021 IFC 108.2 | Fire resistance-rated assemblies Inspection | In-Process Inspection | Fire resistance-rated walls, floor/ceiling systems, barriers, and partitions shall be inspected | OBI | Inspectors need notification and access to inspect each component of the assembly prior to concealment. (ESM Ch.2 Section D4050 9)
Fire Protection | 2021 IBC 1705.18 | Fire Resistant Penetrations and Joints -- Periodic Special inspection | Coordinate with Special inspector | Penetration firestops, fire-resistant joints, and perimeter fire barrier systems | SI
Fire Protection | 2019 NFPA 24 10.10.2.1 | Fire Service Main (Underground) Flushing | In-Process Inspection | Underground piping, including hydrants, shall be flushed before connecting to downstream system piping | OBI
Fire Protection | 2019 NFPA 24 10.9 | Fire Service Main Backfill and Compaction | In-Process Inspection | Backfill and compaction methods per design documents | OBI
Fire Protection | 2019 NFPA 24 10.10.1 | Fire Service Main Certified Material and Test Certificate | Approved Project Submittal | Documentation of commissioning results shall include a Contractor’s Material and Test Certificate for Private Fire Service Mains | FPO | Project Specifications should include as submittal. ESM Ch.2 Section D4050 4.C.2
Fire Protection | 2021 IFC 108.2 | Fire Service Main Flow verification | In-Process Inspection | Fire protection water supply distribution systems and associated appurtenances (block valves, pressure reducing valves, control valves, and fire hydrants) shall be inspected and commissioned to NFPA 24, Standard for the Installation of Private Fire Service Mains and their Appurtenances, and applicable AWWA standards for potable (i.e., domestic) and combined potable/fire water systems where applicable. Testing shall include verification of available fire flow in comparison with original design calculations | OBI | ESM Ch.2 Section D4050 4.C.1
Fire Protection | 2019 NFPA 24 10.10.2.2 2019 NFPA 24 14.1 | Fire Service Main System Hydrostatic Testing | In-Process Inspection | Hydrostatic (leak) testing of piping | OBI
Fire Protection | 2021 IFC 108.2 | Fire Service Main System Rough-in Inspection | Prior to Concealment | Underground piping materials, size and routing per design documents Restraint methods (thrust blocks, retaining fittings) per design documents Appurtenances (hydrants, PIV, FDC, valves, etc.) and locations per design documents | OBI/FP
Fire Protection | 2021 IFC 108.2 | Fire Sprinkler System Rough-in Inspection | Prior to Concealment | Piping materials, size and routing per design documents | OBI
Fire Protection | 2019 NFPA 54 8.1 | Fuel Gas Piping pressure test (see also Plumbing and Mechanical) | In-Process Inspection | Piping system must maintain the test pressure without any reduction throughout the test duration | OBI | 2021 UMC 1302.2, 2021 UPC 1213
Fire Protection | 2021 IBC 110.3.6 | Lath, gypsum board and gypsum panel product inspection | Prior to Concealment | Lath, gypsum board and gypsum panel product inspections shall be made after lathing, gypsum board and gypsum panel products, interior and exterior, are in place, but before any plastering is applied or gypsum board and gypsum panel product joints and fasteners are taped and finished. | OBI | only for fire-resistance-rated assembly or shear assembly
Fire Protection | 2021 IBC 1705.16 | Mastic and Intumescent Fire-Resistant Coatings -- Periodic Special inspection | Coordinate with Special inspector | Application and before concealment | SI
Fire Protection | 2021 IBC 1705.19 | Smoke Control -- Special inspection | Coordinate with Special inspector | Prior to concealment of ductwork and Prior to occupancy | SI
Fire Protection | 2018 NFPA 2001-7 | Special Suppression system acceptance testing | Final Acceptance | Proper clearances between piping and adjacent commodities. Discharge nozzles are properly installed (type, orifice size, orientation, coverage, obstructions, etc.). System actuation and alarm testing. Proper installation of system components (valves, agent storage containers, alarm devices, supervisory devices, gauges and other appurtenances) per design documents. Review enclosure integrity. Proper functionality of control system logic and control functions, releasing panel, auxiliary functions (fan shutdown, power shunt-trip, door closure, damper closure, pre-discharge alarms, abort stations, etc.) per design documents | FPO/OBI
Fire Protection | 2018 NFPA 2001-7 | Special Suppression system piping integrity | In-Process Inspection | Integrity (leak) test of piping | FPO/OBI
Fire Protection | 2018 NFPA 2001-7 | Special Suppression system rough-in inspection | Prior to Concealment | Pipe routing and size per design documents. Piping is properly supported per design documents. Piping is properly braced (seismic restraints installed per design documents). Anchor bolt installations for supports per design documents | OBI
Fire Protection | 2021 IBC 1705.15 | Sprayed Fire-Resistant Materials -- Periodic Special inspection | Coordinate with Special inspector | Application, patching, and before concealment | SI
Fire Protection | 2019 NFPA 13 6.10.2.1.1 | Sprinkler (Underground, Fire) Piping Flushing | In-Process Inspection | All underground piping—from the water supply to the system riser, including lead-in connections and hydrants—must be thoroughly flushed before connecting to downstream fire protection piping | OBI
Fire Protection | 2019 NFPA 13 28.2.5.1 | Sprinkler Riser Backflow Prevention Device Testing | In-Process Inspection | Backflow prevention device(s) forward flow and back flow testing and certification (IAW O&M 406) | OBI
Fire Protection | 2019 NFPA 13 29.7 | Sprinkler System (Modification) Testing | In-Process Inspection | Pressure testing of portion of system that is new/modified. Final connection points are typically tested at normal operating pressure. | FPO | Modifications impacting 20 or fewer sprinklers typically are tested at normal operating pressure
Fire Protection | 2019 NFPA 13 28.2 | Sprinkler System (New) Acceptance Inspection | Final Acceptance | Proper signage, labels and flow arrows on piping and components Proper methods for freeze protection (anti-freeze loops, dry and pre-action configurations, etc.) Review/Approve Contractor’s Material and Test Certificate for Aboveground Piping (2019 NFPA 13 6.10.1) | FPO
Fire Protection | 2019 NFPA 13 28.2 | Sprinkler System (New) Acceptance Testing | In-Process Inspection | Hydrostatic (leak) test of piping Pneumatic (leak) test of Dry Pipe system Flow testing (alarm testing) of system piping Backflow prevention device(s) forward flow and back flow testing and certification (IAW O&M 406) | OBI
Fire Protection | 2019 NFPA 13 16.2.7.7 | Sprinklers List | Approved Project Submittal | Listing of the sprinklers installed within the facility | FPO | Project Specifications should include as submittal. ESM Ch.2 Section D4050 5.A.1
Fire Protection | 2019 NFPA 13 6.10.1 | Sprinklers Material and Test Certificate | Approved Project Submittal | Documentation of commissioning results shall include a contractor’s Material and Test Certificate for Underground Piping (lead-in piping), a contractor’s Material and Test Certificate for Above Ground Piping | FPO | Project Specifications should include as submittal. ESM Ch.2 Section D4050 5.A.1
Fire Protection | 2018 NFPA 22 | Water Tanks for Private Fire Protection - Testing and Acceptance | Approved Project Submittal | Fire protection water supply storage tanks shall be inspected and commissioned per NFPA 22, Standard for Water Tanks for Private Fire Protection, and applicable American Water Works Associations (AWWA) standards for potable water storage tanks. Tank manufacturer/erector and/or representative shall document inspection and commissioning results within an inspection report. | FPO | Project Specifications should include manufacturer's field services and submittal reports. ESM Ch.2 Section D4050 4.0.A
Mechanical | 2021 UMC 603.9.2 | Duct Leakage Tests | In-Process Inspection | Ductwork shall be leak-tested in accordance with the SMACNA HVAC Air Duct Leakage Test Manual. Representative sections totaling not less than 10 percent of the total installed duct area shall be tested. | OBI | Exception: Transfer air duct operating at less than 1 inch of water column.
Mechanical | 2021 UMC 105.2 | Final inspection - Mechanical |  | Final inspection shall be made upon completion of the installation. | OBI
Mechanical | 2021 UMC 1302.2 | Fuel Gas Piping Testing (see also Fire Protection task) | In-Process Inspection | All piping system shall be tested prior to initial operation | OBI | 2019 NFPA 54-8.1
Mechanical | 2021 UMC 1205.2 | Hydronics Pressure Testing | In-Process Inspection | System piping and components shall be tested | OBI | 2020 ASME B31.9 937 2024 ASME B31.1 137 (Steam Distribution Only)
Mechanical | 2021 UMC 1405.2.2 | Process Piping Testing (see Pressure Safety row - B31.3 instead) | Final Acceptance | Final inspection shall include a pressure test | OBI | 2024 ASME B31.3 345
Mechanical | 2021 UMC 1116.2 | Refrigeration Systems Testing (see Pressure Safety row - B31.5 instead) | Final Acceptance | Refrigerant-containing parts of a system that is field-erected shall be tested and proved tight after complete installation and before the operation. | OBI | 2022 ASME B31.5 538
Mechanical | 2021 UMC 105.2 | Rough-in inspection - Mechanical | Prior to Concealment | Rough-in inspection shall be made prior to the installation of wall or ceiling membranes. | OBI
Mechanical | 2021 UMC 105.3 | System Testing - Mechanical | Final Acceptance | Tests shall be conducted in the presence of the AHJ or the AHJ’s duly appointed representative. | OBI
Mechanical | 2021 UMC 105.2 | Underground inspection - Mechanical | Prior to Concealment | The underground inspection shall be made after trenches or ditches are excavated and bedded, piping installed, and before backfill is put in place. | OBI
Plumbing | 2021 UPC 603.4.2 | Backflow Prevention Assembly Testing (other than sprinkler riser) | In-Process Inspection | Devices or assemblies shall be tested in accordance with recognized standards | OBI
Plumbing | 2021 UPC 723 | Building Sewer Test | Final Acceptance | Building sewers shall be tested | OBI
Plumbing | 2021 UPC 105.2 | Final inspection - Plumbing | Final Acceptance | Final inspection shall be made upon completion of the installation. | OBI
Plumbing | 2021 UPC 1213 | Fuel Gas Piping Testing (see also Fire Protection task) | In-Process Inspection | Prior to acceptance and initial operation, all piping installations shall be pressure tested | FPO/OBI | 2019 NFPA 54-8.1
Plumbing | 2021 UPC 105.2 | Rough-in inspection - Plumbing | Prior to Concealment | Rough-in inspection shall be made prior to the installation of wall or ceiling membranes. | OBI
Plumbing | 2021 UPC 712 | Sanitary Drainage and Vent System Testing | In-Process Inspection | The piping of the plumbing, drainage, and venting systems shall be tested | OBI
Plumbing | 2021 UPC 1107.1 | Storm drainage testing | In-Process Inspection | New building storm drainage systems and parts of existing systems that have been altered, extended, or repaired shall be tested | OBI
Plumbing | 2021 UPC 105.3 | System Testing - Plumbing | In-Process Inspection | Tests shall be conducted in the presence of the AHJ or the AHJ’s duly appointed representative. | OBI
Plumbing | 2021 UPC 105.2 | Underground inspection - Plumbing | Prior to Concealment | The underground inspection shall be made after trenches or ditches are excavated and bedded, piping installed, and before backfill is put in place. | OBI
Plumbing | 2021 UPC 609.4 | Water supply and distribution testing - Plumbing | In-Process Inspection | Upon completion of a section or of the entire hot and cold water supply system, the system shall be tested. | OBI
Pressure Safety | ASME B31.1 136.1 ASME B31.3 340 ASME B31.5 537 ASME B31.8 841.2.2 ASME B31.9 936.1, 936.2 | Owner's Inspection of B31 Code Piping Note, UPC 105.3 (Plumbing) & UMC 105.3 (Mechanical) inspections are different; ref. them | Coordinate with Owner's Inspector | B31.3 para 340.2: "It is the owner's responsibility, exercised through the owner’s Inspector, to verify that all required examinations and testing have been completed and to inspect the piping to the extent necessary to be satisfied that it conforms to all applicable examination requirements of the Code and of the engineering design." The above generally also applies to the other B31 codes; however, see specifics per their listed paragraphs (e.g., for nat. gas, ASME B31.8 has more specific inspection provisions for installation of steel pipelines and mains). | OBI | The Owner's Inspector has authority granted by Code to access any place where work related to B31 piping installation is being performed, audit examinations, perform examinations of their own, etc. They do not need to be present for any work, but historically at LANL OIs witness all pressure and leak testing.
Structural | 2021 IBC 1705.2.2 | CFS Deck -- Continuous Special Inspection | Coordinate with Special inspector | Material, placement, welding and fastening | SI | See exceptions under 1705.2
Structural | 2021 IBC 1705.2.2 | CFS Deck -- Periodic Special Inspection | Coordinate with Special inspector | Material, placement, welding and fastening | SI | See exceptions under 1705.2
Structural | 2021 IBC 1705.2.3 | Cold-formed steel trusses -- Special Inspection | Coordinate with Special inspector | Temporary and permanent individual truss member restraint/bracing | SI | applicable only to trusses spanning 60 feet or greater
Structural | 2021 IBC 1705.3 | Concrete Construction -- Continuous Special inspection | Coordinate with Special inspector | Welds, post-installed anchors, strength, slump, air, temperature, application, and prestressing. | SI | See exceptions under 1705.3. Where P-I anchors are shown as seismically-exempt, no SI required.
Structural | 2021 IBC 1705.3 | Concrete Construction -- Periodic Special inspection | Coordinate with Special inspector | Reinforcement, welds, anchors cast-in or post-installed, design mixes not pre-approved, curing, erection of precast members, concrete strength, and formwork | SI | See exceptions under 1705.3. Where P-I anchors are shown as seismically-exempt, no SI required.
Structural | 2021 IBC 110.3.2 | Concrete slab and under-floor inspection | Prior to Concealment | Concrete slab and under-floor inspections shall be made after in-slab or under-floor reinforcing steel and building service equipment, conduit, piping accessories and other ancillary equipment items are in place, but before any concrete is placed or floor sheathing installed, including the subfloor. | OBI
Structural | 2021 IBC 1705.10 | Fabricated Structural Items -- Periodic Special inspection | Coordinate with Special inspector | Offsite Fabrication Inspection | SI
Structural | 2021 IBC 110.3.1 | Footing and foundation inspection | Prior to Concealment | Footing and foundation inspections shall be made after excavations for footings are complete and any required reinforcing steel is in place. For concrete foundations, any required forms shall be in place prior to inspection. Materials for the foundation shall be on the job, except where concrete is ready mixed in accordance with ASTM C 94, the concrete need not be on the job. | OBI
Structural | 2021 IBC 110.3.4 | Frame inspection | Prior to Concealment | Framing inspections shall be made after the roof deck or sheathing, all framing, fire-blocking and bracing are in place and pipes, chimneys and vents to be concealed are complete and the rough electrical, plumbing, heating wires, pipes and ducts are approved. | OBI
Structural | 2021 IBC 1705.4 | Masonry Construction -- Continuous Special inspection | Coordinate with Special inspector | Welding, prestressing, grout and anchors | SI | See exceptions under 1705.4. Where P-I anchors are shown as seismically-exempt, no SI required.
Structural | 2021 IBC 1705.4 | Masonry Construction -- Periodic Special inspection | Coordinate with Special inspector | Grout, mortar, anchoring, structural elements, rebar, pre-stressing tendons | SI | See exceptions under 1705.4. Where P-I anchors are shown as seismically-exempt, no SI required.
Structural | 2021 IBC 1705.2.3 | Open-web Steel Joists and Joist Girders -- Periodic Special Inspection- | Coordinate with Special inspector | End connections and bridging | SI | See exceptions under 1705.2
Structural | 2021 IBC 1705.13 | Seismic Resistance -- Special inspection | Coordinate with Special inspector | Structural Steel Systems, CFS light-frame construction, Designated Seismic Systems, and Plumbing, Mechanical and Electrical Components | SI | See exceptions under 1705.13
Structural | 2021 IBC 1705.14 | Seismic Resistance -- Testing | Coordinate with Special inspector | Structural Steel Systems, CFS light-frame construction, Designated Seismic Systems, and Plumbing, Mechanical and Electrical Components | SI
Structural | 2021 IBC 1705.6 | Soils -- Periodic Special inspection | Coordinate with Special inspector | Excavations and subgrade | SI | See exceptions under 1705.6
Structural | 2021 IBC 1705.6 | Soils -- Continuous Special inspection | Coordinate with Special inspector | Backfill | SI | See exceptions under 1705.6
Structural | 2021 IBC 1705.2.1 | Structural Steel -- Continuous Special Inspection | Coordinate with Special inspector | Fabrication, Installation, Welding and High strength Bolting | SI | See exceptions under 1705.2
Structural | 2021 IBC 1705.2.1 | Structural Steel - Periodic Special Inspection | Coordinate with Special inspector | Fabrication, Installation, Welding and High strength Bolting | SI | See exceptions under 1705.2
Sustainable Design | 2021 IBC 110.3.9 | Energy efficiency inspections | Prior to Concealment | Inspections shall be made to determine compliance with Chapter 13 and shall include, but not be limited to, inspections for: envelope insulation R- and U-values, fenestration U-value, duct system R-value, and HVAC and water-heating equipment efficiency. | OBI | Additional inspections may be needed for LEED and/or Guiding Principles when required (ref. ESM/TSM Ch. 14)

## Legend, Defn's, and WBS Example
Legend (all sheets/tabs)
CONSTRUCTOR OR CONSTRUCTOR-HIRED UNLESS OTHERWISE INDICATED
CO |  | Constructor
QC or QCI |  | Quality Control representative -- Constructor's QC Inspector (e.g., IQPA-QSS for LANL self-perform)
TA |  | Testing Agency (LANL-approved per ESM Ch. 16 IBC-TIA) or Manufacturer's Technical Representative
LANL or LANL-HIRED
CEIO |  | Chief Electrical Inspector's Office (LANL OSH-ISH)
Cx |  | Commissioning Agent (ref. ESM/TSM Ch. 15)
FE |  | Field Engineer
FPO |  | Fire Protection Office
LCA |  | LANL Commissioning Authority (STUPCOMM; per ESM/TSM Ch. 15)
TEL |  | Telcom Representative (ISD-TS, was NIE)
OBI |  | Owners Building Inspector (LANL; ref. ESM Ch. 16 IBC-IP)*
UI |  | Utilities and Infrastructure Representative
SI |  | Special Inspector (IBC Ch. 17)
* Note on OBIs: Includes jurisdiction inspection to codes and their invoked standards. May also include owner observation that design is met when not performed by LANL-contracted EOR.
Definitions (all sheets/tabs)
Abbreviations and definitions are maintained in the Conduct of Engineering Glossary, GLOS-COE-1. The following are included for convenience or are specific to this document. |  |  |  | GLOS-COE-1
Hold Point |  | A mandatory verification that cannot be passed without being specifically released by the entity that established the Hold Point in the template. All code-driven tasks are Hold Points, and most Spec-Based ones default to this. Nominal notification lead time needed is 48 hours.
In-Process Inspection |  | For code-driven tasks, typically occurs with an activity that is progressing but before the subtask is completely finished -- and does not clearly fit another category (e.g., Final, Prior to Concealment, special inspection, others).
QC Verification |  | Within the Spec-Based tasks, an in-process formal documentation of adherence to standards identified in the Specification, typically by Constructor or third-party they engage.
Inspection |  | Documented verification of adherence to requirements defined in Project-applicable codes and standards, typically by LANL.
Testing |  | Documented verification process by an LBO-approved testing agency or Manufacturer's Technical Representative
Witness Point |  | A point in the process where an inspection, test, or activity point is reached that requires notification of the designated individual that the items are available for the designated inspection, test, or activity. Work may proceed past the point and work is not required to stop if the requester is not present. Nominal notification lead time needed is 48 hours.
Work Breakdown Structure (WBS) Style TIP Example (below)
Column Heading |  | Column Heading Explanations
WBS |  | Unique Task/Summary Identification Number
WBS Predecessors |  | WBS of Task or Summary that must be completed prior to completion of line task/summary
Task Name |  | Descriptive Name of Task/Summary
Task Type |  | Categorization of Task
Hold Point |  | Identification if Task is a hold point
Responsible Party |  | Party responsible for Task or release of hold point
Requirement Reference |  | Requirement basis for task
Specification |  | Requirement basis for task
Report ID |  | Unique project record identifier for documentation of hold point to be entered/tracked during execution of project
Level | Description | WBS Level Explanations
Level 1 | Discipline | High Level Deliverable of all systems related to the noted Discipline, and having a Final Acceptance Inspection (FAI)
Level 2 | DFOW | Definable Feature of Work - Structure, System, or Component (SSC) installed as part of the overall project scope
Level 3 | Specification | Requirements for the named SSC grouped by applicable specification section
Level 4 | Task Group | Grouping of applicable requirements and tasks into summary tasks as needed
Level 5 | Task | Requirements and high level tasks providing sequence of execution and highlighting predecessors and successors of Hold Points
5 or 1 | Task or FAI | Task-level 5 test or inspection, or Final Acceptance Inspection of the Level 1 Discipline
WBS | WBS Predecessors | Task Name | Task Type | Hold Point | Responsible Party | Requirement Reference | Specification | Report ID
1 |  | Electrical
1.1 |  | Building Grounding Electrode System
1.1.1 |  | [26 0526 Grounding and Bonding for Electrical Systems]
1.1.1.1 |  | Installation of Grounding Electrode System
1.1.1.1.1 |  | Grounding and Bonding installation | Task |  | CO
1.1.1.1.2 | 1.1.1.1.1 | The grounding electrode system must be inspected before the system is covered up, by earthwork, concrete, or building finish. | Inspection | Yes | CEIO | 2021 IBC K106 | 26 0526 3.8.C | [Report ID Required]
1.1.1.1.4 | 1.1.1.1.2 | Bury, conceal, or encase Grounding System | Task |  | CO
1.2 |  | Lightning Protection System
1.2.1 |  | [26 4100 Lightning Protection]
1.2.1.2 |  | Installation of Lightning Protection System
1.2.1.2.1 |  | Lightning Protection Installation | Task |  | CO
1.2.1.2.2 | 1.2.1.2.1 | The Lightning Protection system must be inspected before the system is covered up, by earthwork, concrete, or building finish. | Inspection | Yes | CEIO | 2021 IBC K106 | 26 4100 1.2.A | [Report ID Required]
1.2.1.2.3 | 1.2.1.2.2 | Bury, conceal, or encase Lightning Protection System | Task |  | CO
1.3 |  | Generator
1.3.1 |  | [26 0526 Grounding and Bonding for Electrical Systems]
1.3.1.1 |  | Installation of Grounding Electrode System
1.3.1.1.1 |  | Grounding and Bonding installation | Task |  | CO
1.3.1.1.2 | 1.3.1.1.1 | The grounding electrode system must be inspected before the system is covered up, by earthwork, concrete, or building finish. | Inspection | Yes | CEIO | 2021 IBC K106 | 26 0526 3.8.C | [Report ID Required]
1.3.1.1.4 | 1.3.1.1.2 | Bury, conceal, or encase Grounding System | Task |  | CO
1.3.2 |  | [26 3213 Engine Generators]
1.3.2.2 |  | Engine Generator Installation
1.3.2.2.2 |  | Installation of Engine Generator | Task |  | CO
1.3.2.2.3 | 1.3.2.2.2 | Manufacturer's Field Service | Testing |  | TA |  | 26 3213 3.5 | [Report ID Required]
1.3.3 |  | [26 0533 Raceway and Boxes for Electrical Systems]
1.3.3.1 |  | Raceway and Box Installation
1.3.3.1.2 |  | Install raceways and boxes | Task |  | CO
1.3.3.1.4 | 1.3.3.1.2 | Rough-In Inspection | Inspection | Yes | CEIO | 2021 IBC K106 |  | [Report ID Required]
1.3.3.1.5 | 1.3.3.1.4 | Bury ,conceal, or encase conduit | Task Type |  | CO
1.3.4 |  | [26 0519 Low Voltage Electrical Power Conductor and Cables]
1.3.4.1 |  | Power Cables and Conductors Installation
1.3.4.1.1 |  | Installation of cables and conductors | Task |  | CO
1.3.4.1.4 |  | Termination of cables and conductors | Task |  | CO
1.3.4.1.7 | 1.3.4.1.4[SS] | Witness and document torquing on not less than 10% of each type of connector and terminal | QC Verification | Yes | QC |  | 26 0519 3.8.E.3 | [Report ID Required]
1.4 |  | PP-A
1.4.1 |  | [26 0526 Grounding and Bonding for Electrical Systems]
1.4.1.1 |  | Installation of Grounding Electrode System
1.4.1.1.1 |  | Grounding and Bonding installation | Task |  | CO
1.4.1.1.2 | 1.4.1.1.1 | The grounding electrode system must be inspected before the system is covered up, by earthwork, concrete, or building finish. | Inspection | Yes | CEIO | 2021 IBC K106 | 26 0526 3.8.C | [Report ID Required]
1.4.1.1.4 | 1.4.1.1.2 | Bury, conceal, or encase Grounding System | Task |  | CO
1.4.2 |  | [26 2416 Panelboards]
1.4.2.2 |  | Panelboard Installation
1.4.2.2.2 |  | Installation of Panelboard | Task
1.4.2.2.3 | 1.4.2.2.2 | Authorization to energize | Inspection | Yes | CEIO | P101-13 |  | [Report ID Required]
1.4.2.2.4 | 1.4.2.2.3 | Energize Panelboard | Task |  | CO
1.4.3 |  | [26 0529 Hangers and Supports for Electrical Systems]
1.4.3.2 |  | Hangers and Supports Installation
1.4.3.2.1 |  | Install hangers and supports | Task |  | CO |  | 26 0529 3.1
1.4.4 |  | [26 0533 Raceway and Boxes for Electrical Systems]
1.4.4.2 |  | Raceway and Box Installation
1.4.4.2.2 |  | Install raceways and boxes | Task |  | CO
1.4.4.2.4 | 1.4.4.2.2 | Rough-In Inspection | Inspection | Yes | CEIO | 2021 IBC K106 |  | [Report ID Required]
1.4.4.2.5 | 1.4.4.2.4 | Bury ,conceal, or encase conduit | Task Type |  | CO
1.4.5 |  | [26 0519 Low Voltage Electrical Power Conductor and Cables]
1.4.5.1 |  | Power Cables and Conductors Installation
1.4.5.1.1 |  | Installation of cables and conductors | Task |  | CO
1.4.5.1.4 |  | Termination of cables and conductors | Task |  | CO
1.4.5.1.7 | 1.4.5.1.4[SS] | Witness and document torquing on not less than 10% of each type of connector and terminal | QC Verification | Yes | QC |  | 26 0519 3.8.E.3 | [Report ID Required]
1.4.6 |  | [26 0548.16 Seismic Controls for Electrical Systems]
1.4.6.2 |  | Seismic Control Installation
1.4.6.2.2 |  | Installation of Seismic Control System | Task |  | CO
1.4.6.2.3 |  | Special Inspection of Seismic Control System | Inspection | Yes | SI | SSI 1705.13 |  | [Report ID Required]
1.4.7 |  | [26 0553 Identification for Electrical Systems]
1.4.7.2 |  | Electrical System Identification Installation
1.4.7.2.2 |  | Install Identification for electrical systems | Task |  | CO
2 | 1 | Final Acceptance Inspection - Electrical | Inspection | Yes | CEIO | 2021 IBC 110.3.10 |  | [Report ID Required]