## Master List
Component Type | Manufacturer | Specification | Model Number | MAWP | Recommending User | B31.1 | B31.3 | B31.5 | B31.8 | B31.9 | B31.12 | Pressure System ID | Pressure System Fluid as Used | Size or Range | Comments | Date
Vessel | Amigo |  |  | 171 | VAR-2009-001 | [8 empty] | Shell size 3"
Vessel | Amigo |  |  | 171 | VAR-2009-001 | [8 empty] | Shell size 3.5"
Vessel | Amigo |  |  | 171 | VAR-2009-001 | [8 empty] | Shell size 6"
Vessel | Amigo |  |  | 184 | VAR-2009-001 | [8 empty] | Shell size 7"
Vessel | Amigo |  |  | 171 | VAR-2009-001 | [8 empty] | Shell size 8"
Vessel | Amigo |  |  | 205 | VAR-2009-001 | [8 empty] | Shell size 12"
Rupture disc | OSECO |  | FAS-disc with bolt together flange; lot number T-4308-02 | 125 - 218 @ 72C | VAR-2009-001
Valves | Swagelok |  |  | Various | VAR-2010-001 |  | X | [5 empty] | B31.3 | All
Fittings | Swagelok |  |  | Various | VAR-2010-001 |  | X | [5 empty] | B31.3 | All
Tubing | Swagelok |  |  | Various | VAR-2010-001 |  | X | [5 empty] | B31.3 | All
Tubing | Autoclave Engineering |  | MS15-200 | 14328 | VAR-2010-002 |  | X | [5 empty] | B31.3 | 1/8" x 0.036 thickness
Fitting | Autoclave Engineering | Plug | AP40 | 60000 | VAR-2010-002 |  | X | [5 empty] | B31.3 | 1/4"
Fitting | Autoclave Engineering | Plug | SP20 | 14328 | VAR-2010-002 |  | X | [5 empty] | B31.3 | 1/8"
Fitting | Autoclave Engineering | Sleeve | SSL20 | 14328 | VAR-2010-002 |  | X | [5 empty] | B31.3 | 1/8"
Fitting | Autoclave Engineering | Gland | SMN20 | 14328 | VAR-2010-002 |  | X | [5 empty] | B31.3 | 1/8"
Fitting | Autoclave Engineering | Gland | AGL40 | 60000 | VAR-2010-002 |  | X | [5 empty] | B31.3 | 1/4"
Fitting | Autoclave Engineering | Collor | ACL40 | 60000 | VAR-2010-002 |  | X | [5 empty] | B31.3 | 1/4"
Flex hoses | Swagelok |  | FM, FJ, FL, T, X, S, C, N, W, F, U | 3100 | VAR-2011-089 |  | X | [5 empty] | B31.3 | All
Flex hoses | Spear | double o-rings to be EPDM or Viton®, Safe-T-Shear stem only | True Union 2000 Industrial Type | Various | VAR-2011-115 |  | X | [5 empty] | B31.3/Water | 1/2" to 8"
Valve | Spear | PVC | True Union 2000 Industrial Type Ball Valve | 235 for 1/2"-2"; 150 for 2 1/2"-8" | VAR-2011-115 |  | X | [5 empty] | B31.3/Water | 1/2" to 8"
Valve | Spear | PVC | True Union 2000 Industrial Ball Check Valves | 235 for 1/2"-2"; 150 for 2 1/2"-8" | VAR-2011-115 |  | X | [5 empty] | B31.3/Water | 1/2" to 8"
Valve | Spear | PVC | True Union 2000 pneumatic actuated ball valves | 235 for 1/2"-2"; 150 for 2 1/2"-8" | VAR-2011-115 |  | X | [5 empty] | B31.3/Water | 1/2" to 8"
Diaphram Valve | Spear | PVC & CPVC | Weir type, dv-2-1108 | 235 for 1/2"-2"; 150 for 2 1/2"-4"; 100 for 6"; 75 for 8" | VAR-2011-115 |  | X | [5 empty] | B31.3/Water | 1/2" to 8"
Strainer | Spear | PVC | Y-type, YS-2-0406 | 150 for 1/2"-2"; 90 for 3" to 4" | VAR-2011-115 |  | X | [5 empty] | B31.3/Water | 1/2" to 4"
Tubing | LMI Pumps | Linear low density | LLDPE-PE1000 | 459 | VAR-2012-025 |  | X | [5 empty] | B31.3
Strainers | Poly-Flo | HDPE | Dual containment | 150 for 1/2"-2"; 90 for 3" to 4"; | VAR-2012-045 |  | X | [5 empty] | B31.3 | 2" x 3"; 4" x 6"
Piping | Poly-Flo | HDPE | Dual containment | 50 | VAR-2012-045 | [7 empty] | B31.3 Category M
Fitting | NIBCO/Chemtrol | PDVF Schedule 80 | Socket fusion | 580 @ 73C | VAR-2012-097 | [7 empty] | B 31.3 Category M | 1/2"
Valve | NIBCO/Chemtrol | PDVF Schedule 80 | Socket fusion/Ball valve and flanges | 495 @ 73C | VAR-2012-097 | [7 empty] | B 31.3 Category M | 1/2"
Flow Meter | King Instruments | Stainless Steel | 7710 Series Flow Meter | 1500 | VAR-2012-097 |  | X | [5 empty] | B31.3 Category Normal
Fitting | AnvilStar |  | Gruvlok 7046 Series Saddle Tee | 175 | VAR-2012-097 |  | X | [5 empty] | B31.3 Category D | 1, 1- 1/4, 1- 1/2
Flow Meter | King Instruments | Polysuflone | 7330 Flow Meter | 150 @ 54C | VAR-2012-098 |  | X | [5 empty] | B31.3 Category D
Valve | PROCO | Molded Spherical | Molded Spherical Joint Style 240/242 | 225 @ 170F | VAR-2012-098 |  | X | [5 empty] | B31.3 Category D | 1 1/4" and 1 1/2"
Valves | Asahi | PVC, Specification D1784 | Gate Valves, Schedule 40 | 100 | VAR-2012-106 |  | X | [5 empty] | B31.3 | 4" & 6"
Valves | Saint-Gobain | PFA | TSPF35-0250-047-50 | 100 | VAR-2012-123 |  | X | [5 empty] | B31.3, Hydrogen | 1/8" ID, 1/4" OD
Tubing | Parker Hannifin | PFA Compressions |  | 62.5 | VAR-2012-123 |  | X | [5 empty] | B31.3, Hydrogen | 1/4"
Valve | Nupro | Stainless steel | 304-24VFBG | 62 psia | VAR-2013-086 |  | X | [5 empty] | Hydrogen, Tritium gas |  | Vacuum valve
Valve | Varian | Stainless steel | L8679-301 | 62 psia | VAR-2013-086 |  | X | [5 empty] | Hydrogen, Tritium gas |  | Vacuum valve
Valve | Varian | Stainless steel | L6591-301 | 62 psia | VAR-2013-086 |  | X | [5 empty] | Hydrogen, Tritium gas |  | Vacuum valve
Tubing | Swagelok | Stainless Steel |  | See Table 1 | VAR-2014-022 |  |  |  |  | X |  |  | B31.9 | See Table 1
Fitting | Swagelok | Stainless Steel |  | See Table 1 | VAR-2014-022 |  |  |  |  | X |  |  | B31.9 | See Table 1
Valves | Swagelok | Stainless Steel |  |  | VAR-2014-022 |  |  |  |  | X |  |  | B31.9 | See Table 1
Tubing | Swagelok | Brass/Copper |  | See Tables 2 & 3 | VAR-2014-022 |  |  |  |  | X |  |  | B31.9 | See Tables 2 & 3
Fitting | Swagelok | Brass/Copper |  | See Tables 2 & 3 | VAR-2014-022 |  |  |  |  | X |  |  | B31.9 | See Tables 2 & 3
Valves | Swagelok | Brass/Copper |  |  | VAR-2014-022 |  |  |  |  | X |  |  | B31.9 | See Tables 2 & 3
Tubing | Mueller/Streamline | Copper |  | See Tables 4 & 5 | VAR-2015-011 |  | X | X |  | X |  |  |  | See Tables 4 & 5 |  | 2014-11-24
Fittings | Mueller/Streamline | Copper |  | See Tables 4 & 5 | VAR-2015-011 |  | X | X |  | X |  |  |  | See Tables 4 & 5 |  | 2014-11-24
Filters | Swagelok |  | F, TF, FW, FC | 350 | VAR-2015-030 |  |  |  |  | X |  |  | Liquid 350 @ 250F, Steam and Condensate @ 366, Compressed air and gas 150 psig @ 200 F |  |  | 2015-04-29
Y Fittings | CGP Manufacturing Inc. | 2 x 1.5x1.5 S40 SMLS WYE A182 F316L |  | 1989 psig @100 F | VAR-2015-036 |  | X | [5 empty] | MAWP drops as a function of temperatur to the upper temperature of 1300 F | See tables in variance for T vs. P |  | 2015-04-13
Y Fittings | CGP Manufacturing Inc. | 1.5 S40 SMLS WYE A182 F316L |  | 2359 psig @100 F | VAR-2015-036 |  | X | [5 empty] | MAWP drops as a function of temperatur to the upper temperature of 1300 F | See tables in variance for T vs. P |  | 2015-04-13
ASME Stamped Relief Device | All |  |  | >15 psig | VAR-2015-045 |  | X | [7 empty] | Allowance to use ASME Stamped Relief Devices as Listed items | 2015-05-06
ASME Stamped Relief Device | All |  |  | >15 psig | CIR-2015-005 |  |  |  |  | X |  |  |  |  | Allowance to use ASME Stamped Relief Devices as Listed items | 2015-06-18
Thermowells | Winters |  |  | 150 psig @ 70 F | VAR-2015-053 |  |  |  |  | x |  |  | Water | 1/4, 1/2, 1 in NPT |  | 2015-06-15
Dielectric | Waterway Dielectric Unions |  |  | 150 psig @ 70 F | VAR-2015-053 |  |  |  |  | x |  |  | Water | 3 inch |  | 2015-06-15
Test Plugs | Pete's Plug |  |  | 150 psig @ 70 F | VAR-2015-053 |  |  |  |  | x |  |  | Water | 1/4 in |  | 2015-06-15
Air Vents | Spirax Sarco |  | 13WS | 150 psig @ 70 F | VAR-2015-053 |  |  |  |  | x |  |  | Water | 3/4 x 3/8 inch |  | 2015-06-15
Strainer | Eaton | ASTM B16.1 | 510 | 150 psig @ 70 F | VAR-2015-053 |  |  |  |  | x |  |  | Water | 8 to 24 Pipe |  | 2015-06-15
Strainer | Eaton | ASTM B16.1 | 72 | 150 psig @ 70 F | VAR-2015-053 |  |  |  |  | x |  |  | Water | 2 to 6 Pipe |  | 2015-06-15
Butterfly Valves | Bell & Gosset | ASTM B16.1, ASTM A126 | 58B | 150 psig @ 70 F | VAR-2015-053 |  |  |  |  | x |  |  | Water | 12 inch |  | 2015-06-15
Control Valves | Griswold |  |  | 150 psig @ 70 F | VAR-2015-053 |  |  |  |  | x |  |  | Water | 16 inch pipe |  | 2015-06-15
Nuts and Bolts | SAE J429 |  |  | 150 psig @ 70 F | VAR-2015-053 |  |  |  |  | x |  |  | Water | 5/8 inch |  | 2015-06-15
ConFlat Flanged Fittings |  | CF flanges and flanged fittings (not valves) |  | 50 psig 60-120 F | VAR-2015-032 |  | X | [6 empty] | 1 1/3 and 2 3/4 | CF with copper gaskets; non-cyclic, no dynamic loads; Torque Requirements are 7 ft-lb for 1 1/3" and 12 ft-lb for 2 3/4" (see www.lesker.com/newweb/flanges/flanges_technicalnotes_conflat_1.cfm?) | 2015-06-29
Pipe Fitting | LokRingTM | Carbon Steel Pipe | All | See LokRing sheet | VAR-2016-013 |  | X |  |  | X |  | not specific | not specific | See LokRing sheet
Pipe Fitting | LokRingTM | Stainless Steel Pipe | All | See LokRing sheet | VAR-2016-013 |  | X |  |  | X |  | not specific | not specific | See LokRing sheet
Pipe Fitting | LokRingTM | Stainless Steel Tubing | All | See LokRing sheet | VAR-2016-013 |  | X |  |  | X |  | not specific | not specific | See LokRing sheet
Pipe Fitting | LokRingTM | Copper Tubing | All | See LokRing sheet | VAR-2016-013 |  | X |  |  | X |  | not specific | not specific | See LokRing sheet
Angle Valve | Henry |  | 6475N | 100 | Jessica Garcia |  |  |  |  | X |  |  |  | 5/8 solder connections | Design Pressure 100 psig | 2016-03-04
Flowmeter | Gilmont |  | GF-8531-2227 | 100 | Jessica Garcia |  |  |  |  | X |  |  |  | 1/4 inch MNPT | Design Pressure 100 psig | 2016-03-04
Pressure Regulator | Norgren |  | 11-002-031 | 100 | Jessica Garcia |  |  |  |  | X | [5 empty] | 2016-03-04
Flexhose | Cryofab |  | CFCL | 75 to 1785 depending on size | Todd Siverling |  | X | [6 empty] | inner 0.25 to inner 2.00 | Manufacturer's ratings based on user experience | 2016-03-04
Valve | Sporlan |  | E10S240, E10S350 | 500 | Ryan Smeltzer |  |  | X | [7 empty] | 2016-03-04
Valve | Superior Refrigeration Products |  | WA, WAS, MST | 700 | Ryan Smeltzer |  |  | X | [7 empty] | 2016-03-04
Sight Glass | Sporlan |  | "See-All" | 650 | Ryan Smeltzer |  |  | X | [7 empty] | 2016-03-04
Fill Valve | Parker-Sporlan |  | R | 700 | Ryan Smeltzer |  |  | X | [7 empty] | 2016-03-04
Metal Hose - Vibration Elimination | Universal Metal Hose |  | Anaconda | 360 to 450 by size and material | Ryan Smeltzer |  |  | X | [7 empty] | 2016-03-04
Flexhose | Swagelok | MS-01-180 | PB (Rubber) | 300 at -40 to 70 F | Scott Salisbury |  |  |  |  | X |  | unknown | Compressed Air | 1/4, 3/8, 1/2, 3/4, 1 | Must be derated above 70F | 2016-03-28
Valve | Bellimo |  | G7…(S) | 32-350F | Michael Ladach |  |  |  |  | X |  |  | hydronics | 21/2 to 6 |  | 2016-07-12
Valve | Siemens | compaired to MSS SP-80 | Series 599 Valve | 34-230 F | Ryan Smeltzer |  |  |  |  | X |  | unknown | hydronics | 1/2, 3/4, 1 inch | restricted to HVAC Hot or Chilled Water up to50% glycol | 2016-01-24
Valve | ASCO | 8210 | EF8210G087 | 150 (air and water) 125 (oil) | Heidi Reichert |  | X | [5 empty] | B31.3 | 1/2" | Stainless steel, normally closed, 120VAC solenoid | 2017-04-04
Relief Valve | Rego |  | 9400 | 600 | James Watts |  | X | [5 empty] | Cryogenic (-196 C to +74 C; -320 F to 165 F) | 2.6" x 7/8" 0.062 square inch orfice | Existing systems | 2017-05-22
Expansion Valve | Sporlan | None | Type R | 700 (R410A) 450 (others) | Michael Ladach |  |  | X | [5 empty] | 1/4" - 5/8" Inlet; 3/8" - 1 1/8" outlet |  | 2019-01-09
Fittings | Sporlan | None | ZoomLock Flame-Free Refrigerant Fittings | 600 | Aaron Hobson |  |  | X | [5 empty] | 1/4" through 1-3/8" (SEE COMMENTS) | Limited to ONLY components in the size range tested and approved via UCE form 5C. The exhaustive list includes: Couplings, Slip Couplings, Caps, SAE Flares1, 90 Elbows2, 45 Elbows3. Note 1: 1/4" through 3/4" only Note 2: 1-3/8" not permitted Note 3: 1/4" 45 Elbows not available | 2019-03-21
Coupling | Victaulic | AWWA C606 Grooved Fittings | Style 77 Coupling | 1000 up to 6 inch | Robert Payment |  | X |  |  |  |  | Many; TA50 | RLW | Up to 6 inch NPD | EPDM Gasket Material; ASTM A536 Ductile Iron | 2019-07-29
Coupling | Smith-Cooper | AWWA C606 Grooved Fittings | Fig. 65SF and 66SF | 1000 up to 6 inch | Robert Payment |  | X |  |  |  |  | Many; TA50 | RLW | Up to 6 inch NPD | EPDM Gasket Material; ASTM A536 Ductile Iron | 2019-07-29
Coupling | Anvil International | ASME B16.9 with AWWA C606 | Gruvlok Fittings for Grooved-End Pipe | 1000 up to 6 inch; 800 8-12 inch; 300 14-24 inch | Matt Brazil |  |  |  |  | X |  | Exoscale | Cooling Water | 1 to 24 inch | Rating based on Figure 7001 of Flexible Coupling | 2019-07-29
Expansion Joint | ADSCO Manufacturing LLC | Unlisted | D11PMC-6+6 | 150 @ 500F | Scott Atwater | Main Steam Line to TA3-66 | X |  |  |  |  | Sigma Expansion | Steam | 10 inch flanged | Main Steam Line to TA3-66 | 2019-10-31
Expansion Joint | ADSCO Manufacturing LLC | Unlisted | D11PMC100-3+3 | 150 @ 500F | Scott Atwater | Main Steam Line to TA3-66 | X |  |  |  |  | Sigma Expansion | Condensate | 4 inch flanged | Main condensate Line to TA3-66 | 2019-10-31
High Pressure tubing, fittings, and valves; excluding anti-vibration collet gland assembly | Autoclave Engineering | Type 316/316L | Parker Autoclave Engineers | Lowest 30,000 psig | Heidi Reichert | TA16-202 |  | X |  |  |  | 4782 and others | Tritium | All as shown in manufactuer's materials documented in the 3C-HP Form | Application limited to Q-7 with personnel trained on the assembly process of the fittings. | 2019-12-05
Thermostatic Expansion Valve | Sporlan | None | Type R SERIES (R, ER, SR) | 700 (R410A) 450 (others) | Ryan Keyser |  |  | X |  |  |  | not specific | Refrigerant | All sizes | Type R valve not to be used with R410a. ER and SR can be used with R410a. | 2021-03-15
Solenoid Valve | Sporlan | None | E-series | 700 psig | Ryan Keyser |  |  | X |  |  |  | not specific | Refrigerant | All sizes |  | 2021-03-15
Ball Valve | Superior Refrigeration Products | None | WBS (VRF) series | 800 psig | Ryan Keyser |  |  | X |  |  |  | not specific | Refrigerant | All sizes |  | 2021-03-16
Ball Valve | Mueller | None | CycleMaster | 775 psig (up to 1-5/8") 700 psig (above 1-5/8") | Ryan Keyser |  |  | X |  |  |  | not specific | Refrigerant | All sizes |  | 2021-03-16
Ball Valve | Sporlan | None | EBV, EBVT | 800 psig (up to 2-5/8") 700 psig (above 2-5/8") | Ryan Keyser |  |  | X |  |  |  | not specific | Refrigerant | All sizes |  | 2021-03-16
Ball Valve | Mueller | None | Multi Split | 775 psig | Ryan Keyser |  |  | X |  |  |  | not specific | Refrigerant | All sizes |  | 2021-03-16
Sight Glass | Mueller | None | Sight Glass / Moisture Indicator | 650-700 psig | Ryan Keyser |  |  | X |  |  |  | not specific | Refrigerant | All sizes | Review spec sheet for pressure rating according to size | 2021-03-16
Metal Hose - Vibration Elimination | Parker | None | VABD Vibration Absorber | 190-650 psig depending on material & size | Ryan Keyser |  |  | X |  |  |  | not specific | Refrigerant | All sizes | Review spec sheet for pressure rating according to size | 2021-03-16
Straight Coupling | Autoclave Engineering | 316/316L SS Strain Hardened Cold Drawn ASTM A479-17 Level 2 ASTM A276-17 Condition S ASME SA479 -15 Level 2 | 60F4433 | 5000 psig | Derrick Velasquez/ Larry Padilla |  | X |  |  |  |  | 6958 | Tritium | 1/4" |  | 2023-08-10
Tube OD in. | Table 1. ASME B31.9 Pressure Ratings for Seamless 304/316 ASTM A269 Stainless Steel Tube, for options available in Swagelok MS-01-107
| 0.01 | 0.012 | 0.014 | 0.016 | 0.02 | 0.028 | 0.035 | 0.049 | 0.065 | 0.083
ASME B31.9 MAWP, psig (0-100°F) Applies only to ASTM A269 UNS grades with an allowable stress of 18.75 ksi or higher. (NOTE: For gas services select a tube wall thickness outside of the shaded area. Refer to Swagelok catalog MS-01-107 for details)
0.0625 | 5100 | 6120 | 7140 | 8160 | 10200
0.125 | [5 empty] | 7140 | 8925
0.1875 | [5 empty] | 4760 | 5950 | 8330
¼ | [5 empty] | 3570 | 4463 | 6248 | 8288
0.3125 | [6 empty] | 3570 | 4998 | 6630
0.375 | [6 empty] | 2975 | 4165 | 5525 | 7055
½ | [6 empty] | 2363 | 3308 | 4388 | 5603
0.625 | [7 empty] | 2646 | 3510 | 4482
¾ | [7 empty] | 2205 | 2925 | 3735
0.875 | [7 empty] | 1890 | 2507 | 3201
1 | [8 empty] | 2194 | 2801
1.25 | [9 empty] | 2241
1 ½
2
NPS - Tube OD, in. | Table 2. Copper ASTM B88 Annealed, Tube Wall Thickness (dash indicates size not available) | [7 empty] | ASTM B88 Subtracted Wall Thickness Tolerance, in.
| 0.028 | 0.03 | 0.032 | 0.035 | 0.04 | 0.045 | 0.049 | 0.065
ASME B31.9 MAWP, psig for the annealed condition (S= 6ksi), 0-100°F
¼ - 0.375 | - | 858 | - | 1001 | - | - | - | - | ID reduction = -0.003 and -0.0035
OD increase = 0.0025
½ - 0.625 | 478 | - | - | - | 688 | - | 841 | - | ID reduction = -0.003, -0.004, and -0.005
OD increase = 0.0025
¾ - 0.875 | - | - | 396 | - | - | 560 | - | 806 | ID reduction = -0.003, -0.004, and -0.006
OD increase = 0.003
Tube OD, in. | Table 3. ASME B31.9 Pressure Ratings for ASTM B75 Copper Tube , for options available in Swagelok MS-01-107
| 0.028 | 0.03 | 0.035 | 0.049 | 0.065 | 0.083 | 0.095 | 0.109 | 0.12 | 0.134
MAWP CALCULATED PER ASME B31.9 for the annealed condition (S= 6ksi) 0-100°F (NOTE: For gas services select a tube wall thickness outside of the shaded area. Refer to Swagelok catalog MS-01-107 for details)
0.125 | 2400 | 2592 | 3072
¼ | 1224 | 1320 | 1536 | 2208 | 2952
0.375 |  |  | 1024 | 1472 | 1968
½ |  |  | 768 | 1104 | 1476 | 1896
0.625 |  |  |  | 883 | 1181 | 1517 | 1747
¾ |  |  |  | 728 | 976 | 1248 | 1440 | 1664
1 |  |  |  | 546 | 732 | 936 | 1080 | 1248 | 1368
1.125 |  |  |  |  | 651 | 832 | 960 | 1109 | 1216 | 1216

## Swagelok Flex Hose
This document provides a listing of available Swagelok hose and flexible tubing styles and associated data[1] and indicates whether each is acceptable for code construction at LANL when used within its limits.
[1] Swagelok information taken from publication MS-01-180, May 2011 R5. Variance VAR-2010-001.0 evaluated Swagelok (including the old brands of Whitey, Cajon, and Nupro) to meet the ASME B31.3 304.7.2 requirements, and Swagelok components (tubing, fittings, and valves only) are allowed for use in construction of new code compliant systems at LANL.
Swagelok Flex Hose Series | ASME B31.3 | ASME | Manufacturer | Burst Pressure and Pressure Ratings as a Function of Temperature? | Single Burst Test | No Burst Test | LANL-Wide Approval? | Additional Requirements
| Piping Component? | B31.3-2010 Component Standard | Ratings Based on Code
FM | Yes | BSI BS 6501, Part 1 | B31.1 | No | NA | NA | Yes | None
FJ | Yes | BSI BS 6501, Part 1 | B31.3 | No | NA | NA | Yes | None
FL | Yes | BSI BS 6501, Part 1 | B31.1 | No | NA | NA | Yes | None
CT | Yes | BSI BS 6501, Part 1 | None | No | NA | Yes | No | See A323.2
T | Yes | ASTM F423 | None | Yes | NA | NA | Yes | MAWP based on temperature see A323.2
B | Yes | ASTM F423 | None | No | Yes | NA | No | See A323.2 and A323.2.4
X | Yes | ASTM F423 | None | Yes | NA | NA | Yes | MAWP based on temperature see A323.2
S | Yes | ASTM F423 | None | Yes | NA | NA | Yes | MAWP based on temperature see A323.2
C | Yes | ASTM F423 | None | Yes | NA | NA | Yes | MAWP based on temperature see A323.2
N | Yes | ASTM F423 | None | Yes | NA | NA | Yes | MAWP based on temperature see A323.2
W | Yes | ASTM F423 | None | Yes | NA | NA | Yes | MAWP based on temperature see A323.2
F | Yes | ASTM F423 | None | Yes | NA | NA | Yes | MAWP based on temperature see A323.2
U | Yes | F781 | None | Yes | NA | NA | Yes | MAWP based on temperature see A323.2
PFA | Yes | F781 | None | No | NA | Yes | No | See A323.2
LT | Yes | Unlisted | None | No | Yes | NA | No | See A323.2 and A323.2.4
NG | Yes | Unlisted | None | No | Yes | NA | No | See A323.2 and A323.2.4
7R | Yes | Unlisted | None | No | Yes | NA | No | See A323.2 and A323.2.4
8R | Yes | Unlisted | None | No | Yes | NA | No | See A323.2 and A323.2.4
7N | Yes | Unlisted | None | No | Yes | NA | No | See A323.2 and A323.2.4
8N | Yes | Unlisted | None | No | Yes | NA | No | See A323.2 and A323.2.4
7P | Yes | ASTM D2737 | None | No | Yes | NA | No | See A323.2 and A323.2.4
PB | Yes | Unlisted | None | Yes | NA | NA | No | See A323.2 and A323.2.4

## UL 207, 1963 W.T. Copper Tubing
Maximum Allowable Pressures of UL 207 or UL 1963 Copper Tube at 100°F
Nominal Size (in.) | Outside Diameter (in.) | Pressure Rating (psig) | Solder Joint Rating (psig)
|  |  | Solder Alloy Sn 50 | Solder Alloy 95-5 | Solder Allow E | Solder Alloy HB
0.25 | 0.375 | 894 | 200 | 1090 | 710 | 1035
0.375 | 0.5 | 714 | 200 | 1090 | 710 | 1035
0.5 | 0.625 | 628 | 200 | 1090 | 710 | 1035
0.625 | 0.75 | 630 | 200 | 1090 | 710 | 1035
0.75 | 0.875 | 580 | 200 | 1090 | 710 | 1035
1 | 1.125 | 490 | 200 | 1090 | 710 | 1035
1.25 | 1.375 | 435 | 175 | 850 | 555 | 805
1.5 | 1.625 | 405 | 175 | 850 | 555 | 805
2 | 2.125 | 360 | 175 | 850 | 555 | 805
2.5 | 2.625 | 335 | 150 | 705 | 460 | 670
Maximum Allowable Pressures of UL 207 or UL 1963 Copper Tube at 150°F
Nominal Size (in.) | Outside Diameter (in.) | Pressure Rating (psig) | Solder Joint Rating (psig)
|  |  | Solder Alloy Sn 50 | Solder Alloy 95-5 | Solder Allow E | Solder Alloy HB
0.25 | 0.375 | 760 | 150 | 625 | 475 | 710
0.375 | 0.5 | 607 | 150 | 625 | 475 | 710
0.5 | 0.625 | 534 | 150 | 625 | 475 | 710
0.625 | 0.75 | 535 | 150 | 625 | 475 | 710
0.75 | 0.875 | 490 | 150 | 625 | 475 | 710
1 | 1.125 | 420 | 150 | 625 | 475 | 710
1.25 | 1.375 | 370 | 125 | 485 | 370 | 555
1.5 | 1.625 | 345 | 125 | 485 | 370 | 555
2 | 2.125 | 305 | 125 | 485 | 370 | 555
2.5 | 2.625 | 285 | 100 | 405 | 305 | 460
GUIDANCE: ASTM B88 or B280 copper tubing that meets wall thickness requirements of UL 207 or UL 1963 (which is less than the W.T. requirements of the ASTM specs) may be used for ASME B31.3, B31.5, and/or B31.9 code construction provided the design prsesure is less than the pressure rating of the tubing defined in column C for the applicable tube size. Note also that if the system is soldered, the pressure rating of the soldered joints may be reduced depending on the solder alloy used. Refer to columns D through G.

## LokRing B31.9
Appendix 1:
LANL LokRing™ Pressure Ratings for B31.9 Service
LokRing™ Carbon Steel Pipe Fittings
LokRing™ | Pipe NPS | ASME B31.1
Size |  | Pipe Schedules 4:1
|  | 40 | 80 | 160
P04 | 1/4” | 1223 | 1653
P06 | 3/8” | 1010 | 1400
P08 | 1/2” | 973 | 1300 | 1203
P12 | 3/4” | 808 | 1100 | 1060
P16 | 1” | 758 | 994 | 913
P20 | 1-1/4” | 620 | 838
P24 | 1-1/2” | 550 | 733
P32 | 2” | 448 | 605
P40 | 2-1/2” | 575 | 850
P48 | 3” | 426 | 565
P64 | 4” | 495 | 660
LokRing™ Stainless Steel Pipe
Fittings
LokRing™ | Pipe NPS | ASME B31.1
Size |  | Pipe Schedules 4:1
|  | 10 | 40 | 80
P04 | 1/4” | 945.25 | 1325 | 1500
P06 | 3/8” | 850 | 1225 | 1437.5
P08 | 1/2” | 1007.5 | 1190 | 1190
P12 | 3/4” | 792.5 | 1052.5 | 1232.5
P16 | 1” | 835 | 920 | 997.5
P20 | 1-1/4” | 612.5 | 675 | 745
P24 | 1-1/2” | 565 | 610 | 610
P32 | 2” | 375 | 550 | 625
P48 | 3” | 230 | 425 | 337.5
LokRing™ Stainless Steel Tube
Fittings
Tube Wall Thickness Measured in Inches 4:1; B31.1
Tube OD | Size | 0.035 | 0.049 | 0.065 | 0.083 | 0.095 | 0.109 | 0.12
1/4" | T04 | 1275 | 1875 | 2263
3/8" | T06 | 825 | 1200 | 1413
1/2" | T08 | 650 | 925 | 1068
5/8" | T10 | 525 | 725 | 938
3/4" | T12 | 425 | 600 | 1050 | 1050
7/8" | T14 |  |  | 700
1" | T16 |  |  | 600 | 775
1-1/4” | T20 |  |  | 475 | 600 | 700 | 825
1-1/2” | T24 |  |  | 400 | 500 | 575 | 675 | 750
2” | T32 |  |  | 275 | 375
2-1/2" | T40 |  |  | 225 | 300
LokRing™ Brass Tube
Fittings; B31.1
Nominal Fitting Size | LokRing™ | Tube OD | Qualified Wall |  | Qualified Wall |  | Qualified Wall
|  |  | Thickness K |  | Thickness L |  | Thickness M
|  |  | Wall | LokRing™ | Wall | LokRing™ | Wall | LokRing™
|  |  |  | Pressure Rating (PSI) 4:1 |  | Pressure Rating (PSI) 4:1 |  | Pressure Rating (PSI) 4:1
3/8” | T06 | 0.5 | 0.049 | 487 | 0.035 | 335 | 0.025 | 246
1/2” | T08 | 0.625 | 0.049 | 384 | 0.04 | 311 | 0.028 | 213
5/8” | T10 | 0.75 | 0.049 | 317 | 0.042 | 272 | - | -
3/4” | T12 | 0.875 | 0.065 | 367 | 0.045 | 251 | 0.032 | 175
1” | T16 | 1.125 | 0.065 | 282 | 0.05 | 213 | 0.035 | 145
1¼” | 120 | 1.375 | 0.065 | 229 | 0.055 | 189 | 0.042 | 146
1½” | T24 | 1.625 | 0.072 | 213 | 0.06 | 176 | 0.049 | 142
2” | T32 | 2.125 | 0.083 | 187 | 0.07 | 156 | 0.058 | 129

## LokRing B31.3
Appendix 2:
LANL LokRing™ Pressure Ratings for B31.3 Service
LokRing™Carbon Steel Pipe
Fittings
LokRing™ | Pipe NPS | ASME B31.3 Pipe Schedules 3:1
Size
|  | 40 | 80 | 160
P04 | 1/4” | 2083 | 2937
P06 | 3/8” | 1797 | 2490
P08 | 1/2” | 1730 | 2333 | 2137
P12 | 3/4” | 1433 | 1957 | 1883
P16 | 1” | 1350 | 1767 | 1623
P20 | 1-1/4” | 1103 | 1487
P24 | 1-1/2” | 977 | 1300
P32 | 2” | 797 | 1077
P40 | 2-1/2” | 890 | 990
P48 | 3” | 757 | 823
P64 | 4” | 770 | 1023
LokRing™ Stainless Steel Pipe
Fittings
LokRing™ | Pipe NPS | ASME B31.3
Size |  | Pipe Schedules 3:1
|  | 10 | 40 | 80
P04 | 1/4” | 1510 | 2100 | 2667
P06 | 3/8” | 1200 | 1733 | 2033
P08 | 1/2” | 1430 | 1687 | 1687
P12 | 3/4” | 1127 | 1490 | 1750
P16 | 1” | 1183 | 1307 | 1413
P20 | 1-1/4” | 892 | 970 | 1057
P24 | 1-1/2” | 803 | 867 | 867
P32 | 2” | 533 | 767 | 900
P48 | 3” | 383 | 700 | 568
LokRing™ Stainless Steel Tube
Fittings; B31.3
Pressures for Stainless Steel Tube Wall Thickness Measured in Inches 3:1
Tube OD | Size | 0.035 | 0.049 | 0.065 | 0.083 | 0.095 | 0.109 | 0.12
1/4" | T04 | 1700 | 2500 | 3017
3/8" | T06 | 1100 | 1600 | 1883
1/2" | T08 | 867 | 3700 | 1423
5/8" | T10 | 700 | 967 | 1250
3/4" | T12 | 567 | 800 | 1400 | 1400
7/8" | T14 |  |  | 933
1" | T16 |  |  | 800 | 1033
1-1/4” | T20 |  |  | 633 | 800 | 933 | 1100
1-1/2” | T24 |  |  | 533 | 667 | 767 | 900 | 1000
2” | T32 |  |  | 367 | 500
2-1/2" | T40 |  |  | 300 | 400
LokRing™Brass Tube
Fittings; B31.3
Nominal Fitting Size | LokRing™ | Tube OD | Qualified Wall |  | Qualified Wall |  | Qualified Wall
|  |  | Thickness K |  | Thickness L |  | Thickness M
|  |  | Wall | LokRing™ | Wall | LokRing™ | Wall | LokRing™ Pressure Rating (PSI) 3:1
|  |  |  | Pressure Rating (PSI) 3:1 |  | Pressure Rating (PSI) 3:1
3/8” | T06 | 0.5 | 0.049 | 649 | 0.035 | 447 | 0.025 | 327
1/2” | T08 | 0.625 | 0.049 | 511 | 0.04 | 414 | 0.028 | 283
5/8” | T10 | 0.75 | 0.049 | 422 | 0.042 | 362 | -
3/4” | T12 | 0.875 | 0.065 | 489 | 0.045 | 334 | 0.032 | 234
1” | T16 | 1.125 | 0.065 | 375 | 0.05 | 283 | 0.035 | 193
1¼” | 120 | 1.375 | 0.065 | 305 | 0.055 | 252 | 0.042 | 194
1½” | T24 | 1.625 | 0.072 | 283 | 0.06 | 234 | 0.049 | 190
2” | T32 | 2.125 | 0.083 | 249 | 0.07 | 208 | 0.058 | 171