Section 01 4115 
Pressure Safety Submittals

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION section

Rev. 3 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Pressure Safety POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable specification sections from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality sections.

      - ==========================================================

      - This is not a typical LANL master. It is pressure system submittal requirements that the Design Agency must convey to the constructor/fabricator. When applicable, conveying this can be accomplished in several ways:

        - Option 1:  Include this Section in the Specification while ensuring that (a) ​<< 01 4115 - Pressure Safety Submittals>>​ is invoked by the technical sections (in Div. 22, 23, 40, etc.) and (b) those Sections are clear that the submittals discussed here are always sent in per the affected Div. 02-48 section.

        - Option 2:  Including applicable material herein on the drawings and/or in the Spec (again, omit all references to this Section in Spec book) (NOTE: Option 2 is the least desirable option).

      - This document captures LANL’s pressure system submittal requirements once (rather than in multiple sections) for LANL’s convenience in maintaining the requirements.  It is provided as an aid to the design agency for providing a complete, compliant design that LANL can review and accept during the design phase.  Delegation and deferment of said design requires LANL project engineer and pressure safety SME prior approval.

  - *************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

Submittals required for projects involving pressure systems within the scope of LANL ESM Chapter 17 - Pressure Safety.

This Section defines the What and When to submit. The Where to submit applies to Division 02-48 sections. For the How to submit, refer to Section ​​​<< 01 3300 - Submittal Procedures>>​​​​; its Attachment A log further addresses When.

      - ***************************************************************************************

      - Omit/Include specification sections as applicable to project. Div 11 spec sections are not in SpecLink and need to be downloaded from the Engineering Standards specification website to include in the specification package.

      - ***************************************************************************************

RELATED REQUIREMENTS

Section ​​<< 01 3300 - Submittal Procedures>>​​.

Section ​​​<< 01 4444 - Offsite Welding, Brazing and Joining Requirements>>​​​.

Section ​​<< 01 4455 - Onsite Welding, Brazing and Joining Requirements>>​​​.

Section ​​<< 01 4525 - Non-Destructive Examination (NDE) Requirements>>​​

Section ​​<< 01 4631 - Welding, Brazing, and Soldering of Pressure Systems>>​​.

Section ​​<< 01 4731 - Flange Assembly for Pressure Systems>>​​​.​

Section 11 5311.18 - Glovebox Atmosphere Regenerable Purification Systems.

Section ​​​<< 22 0529 - Hangers and Supports for Plumbing Piping and Equipment>>​​​.

Section ​​<< 22 0813 - Testing Piping Systems>>​​.

Section ​​<< 22 1500 - Compressed-Air Systems>>​​​.

Section ​​<< 23 1123 - Facility Natural-Gas Piping>>​​.

Section ​​<< 23 2113 - Hydronic Piping>>​​​.

Section ​​<< 23 2215 - Steam and Condensate Heating Piping and Specialties>>​​.

Section ​​<< 23 2300 - Refrigerant Piping>>​​​.

Section ​​<< 23 6200 - Packaged Compressor and Condenser Units>>​​.

Section ​​<< 23 7413 - Packaged Outdoor Central-Station Air-Handling Units>>​​.

Section ​​<< 23 8123 - Computer Room Air-Conditioners>>​​.

Section ​​<< 25 5000 - Integrated Automated Facility Controls>>​​.

Section ​​<< 33 5100 - Natural Gas Distribution>>​​​.

Section ​​<< 33 6300 - Steam Energy Distribution>>​​.

Section ​​<< 40 0504 - Process Piping>>​​​.

Section ​​<< 43 4113 - Gas and Liquid Pressure Vessels>>​​.

Section ​​<< 43 4116 - Atmospheric Tanks and Vessels>>​​​.

REFERENCE STANDARDS

ASME B31.3 - Process Piping.

ASME BPVC-IV - Boiler and Pressure Vessel Code, Section IV - Rules for Construction of Heating Boilers.

ASME BPVC-VIII-1 - Boiler and Pressure Vessel Code, Section VIII, Division 1: Rules for Construction of Pressure Vessels.

ASTM G93/G93M - Standard Guide for Cleanliness Levels and Cleaning Methods for Materials and Equipment Used in Oxygen-Enriched Environments.

SUBMITTALS

      - NOTE: The following information shall be submitted for all relevant components to the Div 02-48 section to which they apply.

      - NOTE: Submittal documentation defined below shall be identified with the Pressure System Identification Number (PSID).

      - ***************************************************************************************

      - Designer shall select only the submittal types that are applicable to the pressure system(s) in the project.

      - ***************************************************************************************

      - Action Submittals:

        - ******************************************************************************

        - The following subparagraph is a designer-choice based on project-specific requirements.

        - ******************************************************************************

Qualifications of welding and/or brazing procedures and welder/brazer/bonder performance per Sections ​<< 01 4444 - Offsite Welding, Brazing and Joining Requirements>>​ and/or ​<< 01 4455 - Onsite Welding, Brazing and Joining Requirements>>​​.

Qualification of Examiner(s) in accordance with the code of record and per Section ​<< 01 4525 - Non-Destructive Examination (NDE) Requirements>>​.

Qualification of Examination(s) procedures in accordance with the Code of Record and per Section ​<< 01 4525 - Non-Destructive Examination (NDE) Requirements>>​.

        - ******************************************************************************

        - The following four subparagraphs and its subparagraphs are designer-choices based on project-specific requirements.

        - ******************************************************************************

Qualification and evaluation of unlisted components or materials in accordance with the Code of Record.

Certified Materials Test Reports showing material traceability, including weld filler, material tensile test results (where required by the code of record) and conformance with Code of Record.

Unevaluated unlisted components used for construction. Selection of an item outside of the original approved design may be considered unlisted due to its component type or its material of construction. Such items shall be reviewed and approved as shown below:

Items that are unlisted due to component type or material shall be reviewed and accepted in accordance with the project  ASME code of record for appropriate piping installation, and the LANL ESM Chapter 17 - Pressure Safety, Section PS-REQUIREMENTS, 8.2 ASME Unlisted, Specialty, or Unique Components.

Alternately, if non-ASME (NASME) design basis is applied to the design, proof that components are on the reputable manufacturer list; see the LANL ESM Chapter 17 - Pressure Safety, Section PS-REQUIREMENTS, 8.4 NASME Pressure System Design.

If there is an unstamped (non-code) item that is being selected or substituted where a stamped item is required, justification and the code-equivalent documentation must be supplied. See LANL ESM Chapter 17 - Pressure Safety, Section PS-REQUIREMENTS, 7.7 Application Of Codes, Standards, or Documents Not Invoked by 10 CFR 851.

If a component (e.g., valve, pressure regulator, etc.) or pressure source (e.g., pump, compressor, gas cylinder) is changed during construction as a substitute which has an impact to the overpressure protection evaluation, the evaluation shall be resubmitted to account for evaluation input changes.

        - ******************************************************************************

        - The following two subparagraphs and its subparagraphs are designer-choices based on project-specific requirements.

        - ******************************************************************************

An overpressure protection evaluation for every pressure system for any temporary configurations (e.g., pressure/leak testing).

This evaluation may be a comparison using the LANL approved calculation. This calculation may be a comparison using the LANL-approved calculations, CALC-10-00-786-PSS-GEN-00001 Rev.0 or CALC-11-00-786-PSS-GEN-246 Rev.0 (or successors) for gas flows, CALC-10-00-786-PSS-GEN-207 Rev. 0 (or successor) for steam. MS Excel workbooks based on the calculations referenced are available via the LANL ESM Chapter 17 - Pressure Safety, Reference Data(LANL internal only).

Deferred design information within the scope of pressure safety as applicable. Examples include piping supports, code evaluations like flexibility analyses, and flange assembly directions.

Informational Submittals at Closeout:

      - Pressure system fabrication documentation including information of "as-built" condition of pressure system(s), but are not limited to:

        - The fabricator shall provide the information with updated drawings or sketches as appropriate.

The Design Pressure or pressure rating and Design Temperature or temperature rating for the bill of materials (all components) for the pressure system(s).

        - ******************************************************************************

        - The following two subparagraphs are designer-choices based on project-specific requirements.

        - ******************************************************************************

Documentation of welds/brazes as required by the design and the code of record. If weld maps are used, they shall indicate the physical location of the weld.

Weld/braze examination forms in accordance with LANL ESM Chapter 13 - Welding, Joining & NDE.

Examination reports.

Other non-destructive evaluation (NDE) data reports

Inspection reports. LANL Form 2305, Pressure System Inspection, may be used to document the results of the inspection.

Certifications required by the Code of Record; for example, <<ASME B31.3>> Section 341.4.1 requires the examiner to provide the Inspector with a certification that all the quality control requirements of the Code and of the engineering design have been carried out.

Mandatory records required by the Code of Record.

        - ******************************************************************************

        - The following subparagraph is  designer-choices based on project-specific requirements.

        - ******************************************************************************

Piping component and materials evaluation as required by the code of record where unlisted components are used for construction; see Paragraph << 1.4.A.6; or  ______>> regarding "Unevaluated unlisted components" for more information.

        - ******************************************************************************

        - The Pressure Safety Implementation Plan (PSIP) will help the Design Agency define in the design (specs or drawings) the required fabricator submittals. Reference ESM Chapter 17, Pressure Safety, Section PS-REQUIREMENTS, 2.0 Pressure Safety Implementation Plan.

        - ******************************************************************************

Pressure safety submittals required by ESM Chapter 17, Pressure Safety, Section PS-REQUIREMENTS, and Attachment REQ-2, New or Modified System Design Document Requirements.

          - **********************************************************************

          - The following two subparagraphs and its subparagraphs are designer-choices based on project-specific requirements.

          - **********************************************************************

For all pressure vessels, boilers, and <<ASME BPVC-IV>>​ 'HLW’ water heaters:

A complete copy of the manufacturer’s data report for code-stamped items (pressure vessels (U), power boiler (S), heating boiler (H), etc.) with the national board numbering and registration. A complete copy includes partial data reports for the supplied items. For example, an ASME Form U or U-1 manufacturer’s data report for an <<ASME BPVC-VIII-1>> <<ASME BPVC>>for a compressor air receiver with national board registration number assigned on the data report.

Relief device record of conformance (e.g., ‘UV’ stamp, etc.).

Pressure and leak test plans and reports including instrument calibration records. Comply with the LANL ESM Chapter 17 - Pressure Safety, Section PS-REQUIREMENTS, 10.3 Pressure and Leak Testing. LANL Form 2304, Pressure and Leak Test Plan, may be used to document pressure and/or leak test plans and reports.

Records of cleaning. Comply with LANL ESM Chapter 17 - Pressure Safety, Section PS-GUIDE, 8.0 Cleaning. Records of any additional cleaning for each item required by the design for the fabrication, for example oxygen cleaning meeting <<ASTM G93/G93M>>, level 175A or cleaner.

PART 2 - PRODUCTS (Not Used)

PART 3 - EXECUTION (Not Used)

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT is FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 01 4115, REV. 3, DATED APRIL 15, 2026.