Section 01 8734 
Seismic Qualification of Nonstructural Components (IBC)

  - ************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 2 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., SECTION INCLUDES in PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Structural POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-3 and ML-4 projects.  For ML-3 applications, additional requirements may be added if additional confidence is desired. Section << 01 8712 - Seismic Qualification of Equipment – Nuclear-Safety Related>>, which is intended for ML-1 and ML-2 installations, includes such content.

      - ==========================================================

      - Prior to attempting to use this section, the specific seismic performance requirements must be obtained from the appropriate Project Record Document(s) (e.g., Design Basis Document, Requirements and Criteria Document, System Design Description, etc.).

      - This section ensures normal-confidence nonstructural components, systems and equipment (“components”) will achieve the applicable seismic performance requirements.

      - For ensuring “high-confidence components (i.e., SDC-3)” will achieve their seismic performance requirements, use Section << 01 8712 - Seismic Qualification of Equipment – Nuclear-Safety Related>>.

      - This section applies to noncritical components qualified through manufacturer certification and to components requiring Special Certification (e.g., Designated Seismic Systems). It does not apply to components with project-specific designs and documentation.

      - If a component must function after the design-basis earthquake, it is assigned an Importance Factor (Ip) of 1.5, which makes it a DSS (per ASCE 7 Section 11.2).

      - Special certification: Based on ASCE 7-10 Section 13.2.2, ASCE 7-16 Section 13.2.2, and ASCE 7-22 Section 13.2.3, Only the following components in Seismic Design Categories (SDC) C through F require special certification:

        - a. Active mechanical and electrical equipment with Ip = 1.5.

        - b. Components containing hazardous substances with Ip = 1.5.

      - When this Section is used, the project drawings, Statement of Special Inspections (SSI), and component-specific sections (e.g., Section(s) << 23 3101 - HVAC Ducts>>, << 26 2213 - Low Voltage Distribution Transformers>>) shall clearly and consistently identify the components requiring qualification/certification and specify the type (ASCE 7 “special certification” and/or “manufacturer's certification”). The SSI shall include all related content and requirements to ensure consistency and coordination with this Section.

      - The qualification methods in this section include (a) analysis, (b) testing per ASCE 7 Chapter 13 Paragraphs 13.2.2 (shake-table testing) and 13.2.5, and (c) combinations thereof, including supporting tests and analyses as applicable.

      - Qualification using experience data is not covered in this section but is acceptable if performed per ASCE 7 Paragraph 13.2.6. Contact the ESM Structural POC for details if this method is desired or required.

      - For projects in existing facilities with “PC” NPH categorization, refer to the crosswalk in LANL ESM Chapter 5 - Structural, Section I.

  - ************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

This Section applies to noncritical components, Designated Seismic Systems (DSS) not requiring special certification (DOTS), and DSS requiring Special Certification. This Section does not apply to components qualified through project-specific design and documentation.

This Section establishes the minimum technical requirements for seismic qualification of the following nonstructural systems, components, and equipment (hereafter referred to as “components”):

        - ******************************************************************************

        - Edit the following two subparagraphs to clearly state the scope of this Specification Section.

          - Include the first subparagraph if qualification of nuclear SDC-1 and/or SDC-2 components is required.

          - AND/OR

          - Include the second subparagraph, selecting the appropriate risk category, if qualification of non-nuclear components is required.

        - If a component must function after the design-basis earthquake, it is assigned an Importance Factor (Ip) of 1.5, which makes it a DSS (per ASCE Section 11.2).

        - Special certification: Based on ASCE 7-10/ Section 13.2.2, ASCE 7-16 Section 13.2.2, and ASCE 7-22 Section 13.2.3, Only the following components in Seismic Design Categories (SDC) C through F require special certification:

          - a. Active mechanical and electrical equipment with Ip = 1.5.

          - b. Components containing hazardous substances with Ip = 1.5.

        - Customize content to meet specific project requirements.

        - ******************************************************************************

Seismic design category ​​<< SDC-1; and  SDC-2>>​​ ​​<< noncritical;  DSS;  DOTS; and  Click here to select the type of components requiring qualification (e.g., DSS, DOTS, and/or noncritical components).>>​​ components, their supports and attachments, inside or outside of Hazard Category ​​<< 1;  2; and  3>>​​ nuclear facilities.

​<< Noncritical;  DSS;  DOTS; and  Click here to select the type of components requiring qualification (e.g., DSS, DOTS, and/or noncritical components).>>​​​​ Components, their supports and attachments, inside or outside of Risk Category ​<< I;  II;  III; and  IV>>​ buildings and nonbuilding structures.

RELATED REQUIREMENTS

Section ​<< 01 4000 - Quality Requirements - Non-Nuclear>>​

Section ​​<< 01 4216 - Definitions>>​​.

    - **********************************************************************************************

      - The codes/standards listed below are provided for reference only and are not listed within the body of this section. It is a user-choice to include these codes/standards.

      - <<FEMA 461>>, <<IEEE 344>>

      - As indicated in subsequent articles and the references included below, the shake-table-testing required herein is based on AC156. There are two (2) instances in which an alternative basis is permitted:

        - 1. The in-structure horizontal and vertical response spectra exist and a Project desires they be used for the “required response spectrum” for the horizontal and vertical axes, respectively.

        - 2. The component(s) in question is beyond the scope of AC156.

      - If either instance applies, contact the ESM Structural POC to discuss, and agree on, an alternative to AC156 (e.g., IEEE 344 or FEMA 461) for accomplishing shake-table testing.

    - **********************************************************************************************

Reference Standards

ACI CODE-318 - Building Code for Structural Concrete—Code Requirements and Commentary.

ASCE 7 - Minimum Design Loads and Associated Criteria for Buildings and Other Structures.

ASCE 43 - Seismic Design Criteria for Structures, Systems, and Components in Nuclear Facilities.

DOE-STD-1020 - Natural Phenomena Hazards Analysis and Design Criteria for DOE Facilities.

FEMA 461 - Interim Testing Protocols for Determining the Seismic Performance Characteristics of Structural and Nonstructural Components.

ICC (IBC) - International Building Code.

ICC-ES AC156 - Acceptance Criteria for Seismic Certification by Shake-Table Testing of Nonstructural Components.

IEEE 344 - Standard For Seismic Qualification Of Equipment for Nuclear Power Generating Stations.

DEFINITIONS

For definitions and acronyms, refer to COE Glossary of Terms.

Active mechanical and electrical equipment: Equipment that changes state; or has parts that rotate, move mechanically, or are energized during operation. Examples of this type of equipment include pumps, compressors, certain operational valving, electric motors, motor control centers, transformers, switching equipment, UPS, etc.

Actual component response modification coefficient (Ra): Reduced value of the component response modification factor. This coefficient is an indicator of the seismic performance requirements for components that have a seismic design basis (SDB), which are referred to herein as “nuclear components.”

Attachment: Connection of a component to its support(s) and/or the supporting structure.

Base: The level at which the horizontal seismic ground motions are considered to be imparted to the structure.

Certificate of Compliance: See Section << 01 4216 - Definitions>>, definition of certification document. Lacking that Section: A certificate stating that materials and products meet the qualification requirements herein (in PART 2) and that the qualification was done in accordance with the qualification methods herein (in PART 3). adapted from <<ICC (IBC)>>)

Components: Nonstructural components, equipment, and systems that are permanently attached to structures. These can be nuclear components, or “non-nuclear components (i.e., component that doesn’t have an SDB).”

Component Importance Factor (Ip): An indicator of the seismic performance requirements for components.

Ip = 1.0 for SDC-1 nuclear components, and for noncritical/unessential non-nuclear components.

Ip = 1.5 for SDC-2 nuclear components, and for critical/essential non-nuclear components.

      - ***************************************************************************************

      - If a component must function after the design-basis earthquake, it is assigned an Importance Factor (Ip) of 1.5, which makes it a DSS (per ASCE 7 Section 11.2).

      - Special certification: Based on ASCE 7-10 Section 13.2.2, ASCE 7-16 Section 13.2.2, and ASCE 7-22 Section 13.2.3, Only the following components in Seismic Design Categories (SDC) C through F require special certification:

        - a. Active mechanical and electrical equipment with Ip = 1.5.

        - b. Components containing hazardous substances with Ip = 1.5.

      - ***************************************************************************************

Designated Seismic System (DSS): Components that have/are assigned an Ip = 1.5. Only The following components in SDC C to F require special certification: (a) Active mechanical and electrical equipment with Ip = 1.5; (b) Components containing hazardous substances with Ip = 1.5.

      - ***************************************************************************************

      - To prevent consequential damage, consider the functional and physical interrelationship of components, their supports, and their effects on one another so that the failure of an essential or nonessential architectural, mechanical, or electrical component does not cause the failure of an essential component. Each nonessential SSC shall meet at least one of the following criteria:

        - A. Collapse of the nonessential SSC will not cause it to strike an essential SSC

        - B. Collapse of the nonessential SSC will not impair the integrity of an essential SSC.

        - C. The nonessential SSC is analyzed and designed to prevent failure under the same conditions as the essential SSC. Therefore, it is designed as a DSS (Ip = 1.5) but does not require special certification, and can be label as a DOTS.

      - ***************************************************************************************

DSS other than special-certification (DOTS) components: DSS not subject to the special-certification requirements of <<ASCE 7>>​, Section 13.2.2, for instance egress stairways. Only the following components in Seismic Design Categories (SDC) C through F require special certification: (a) Active mechanical and electrical equipment with Ip = 1.5; (b) Components containing hazardous substances with Ip = 1.5.

Design earthquake ground motion/design basis earthquake (DBE): See Design Response Spectrum.

Design Response Spectrum: Per <<ASCE 7>> subject to the requirements of PART 2.

Limit state (LS): An indicator of the seismic performance requirements for nuclear components (i.e., components with an SDB). Specifically, the limit state represents the limiting acceptable condition of a component following the DBE; it ranges from “A” – non-functional/inoperable, but structurally stable (i.e., “position retention”) — through “D” – fully functional/operable.

Noncritical components: All (nuclear and non-nuclear) components that have/are assigned Ip = 1.0.

Nozzle loads: The net forces and moments exerted on equipment nozzles by the connected piping and equipment.

Risk Category (RC): A categorization of buildings and other structures used by the <<ICC (IBC)>> for determination of earthquake loads based on the risk associated with unacceptable performance. It is an indicator of the seismic performance requirements for non-nuclear components (located in/on buildings).

Seismic design basis (SDB): A categorization of components used by the Department of Energy (DOE) for determination of earthquake loads, and for stipulating seismic performance requirements, based on the risk associated with unacceptable performance. An SDB consists of a Seismic Design Category (SDC) and an LS (e.g., SDC-1, LS A; SDC-2, LS C; etc.)1.

      - _______________

      - 1For additional details refer to <<DOE-STD-1020>>-2016  Sections 2.3, 2.4 and 3.1, and <<ASCE 43>>​​-19 Table 1-2

Seismic Design Category (SDC)

DOE/Nuclear components: A function of the severity of adverse radiological and toxicological effects of the hazards that may result from the lack of adequate seismic performance. (i.e., SDC-1 or SDC-2 herein).

- <<ICC (IBC)>>/Non-nuclear buildings/structures: A function of the building’s Risk Category (RC) and the severity of the DBE at the site (i.e., SDC D or C herein).

Seismic performance requirements

Position retention (i.e., component must remain where it was prior to DBE, and must not collapse following DBE).

This performance requirement is applicable to noncritical components.

Position retention and functional/operable.

This performance requirement is applicable to DSS and to DOTS Components; however, the extent of functionality/operability varies.

            - *************************************************************

            - Retain and/or modify the following three subparagraph as applicable per the Project requirements.

            - *************************************************************

DSS consisting of non-nuclear and SDC-2 LS D nuclear components: “Functional/operable” means “no leaks/ spills (for components with hazardous substances2),” or “immediately and fully functional/operable (for all other components),” following the DBE.

            - _______________

            - 2The term “with” used in the context of “components with hazardous substances” shall be understood to include “convey, support or otherwise contain” as applicable

            - *************************************************************

            - In addition editing the bracketed content pertaining to the LS(s) in the following subparagraph, what is meant/required by “Functional/operable” for the applicable LS(s) must be indicated. Specifically, the EOR must indicate the extent of functionality/operability. This must also be indicated for PART 2 Qualification Requirements, Table 2.3

            - ANS 2.26 App. B includes the general intent of LSs B & C for specific types of components, which can be of assistance in trying to determine the specific extent of functionality/operability that must be indicated here (and in Table 2.3 subsequently).

            - This author note applies to the “nuclear-component-portion” of the subsequent subparagraph on functional/operable for DOTS Components except the applicable table is PART 2 is Table 2.4.

            - *************************************************************

DSS consisting of SDC-2 LS ​​<< B; and  C>>​​ nuclear components: “Functional/operable” means ​​<< ______>>​​.

            - *************************************************************

            - What is meant/required by “Functional/operable” for non-nuclear DOTS Components must be indicated in the following subparagraph, specifically, the EOR must indicate the extent of functionality/operability. This must also be indicated in PART 2 Qualification Requirements, Table 2.4.

            - Here are some examples of “the extremes” of functionality/operability for non-nuclear DOTS Components:

            - Functionality/operability is solely component dependent:

              - - The parts and pieces of a fire protection sprinkler system (w/o active components) must function after DBE.

              - - In this instance, since it’s implied by ASCE 7 para. 13.6.8.2 that such a system designed and constructed per NFPA 13 will be functional/operable, qualification by testing need only show/prove position retention.

            - Functionality/operability is component-dependent + other factors:

              - -  The access floor in the main computer room of an emergency operation center must function after DBE, to include small enough deformations such that the people and the nonstructural components that rely on it for support or protection are also “functional/operable.”

              - - The suspended ceiling in a room with highly-toxic materials must not experience deformations that would permit a tile/panel to fall, or that would result in lack of functionality of, say, an HVAC system required to maintain a controlled climate that relies on the ceiling for support.

              - - In these instances, qualification by analysis (i.e., design) or testing showing/ proving position retention + functional/operable might be necessary.

            - *************************************************************

DOTS Components consisting of non-nuclear and SDC-2 LS ​​​<< B; and  C>>​​​ nuclear components: “Functional/ operable” means ​​​<< _______>>​​​.

Special-certification components: DSS that are subject to the special-certification requirements of  <<ASCE 7>> Section 13.2.2. Only the following components in Seismic Design Categories (SDC) C through F require special certification: (a) Active mechanical and electrical equipment with Ip = 1.5; (b) Components containing hazardous substances with Ip = 1.5.

Support: Any item in the load path in-between a component and the supporting structure.

Supporting structure: Typically a building floor, roof, wall, etc.

Abbreviations, Acronyms and Symbols

| ai | Acceleration at level i obtained from a modal analysis |
| --- | --- |
| ap | Component amplification factor |
| Ax | Torsional amplification factor |
| CoC | Certificate of compliance |
| DBE | Design basis earthquake/design earthquake ground motion |
| DOE | Department of Energy |
| DOTS | Designated seismic system other than special certification, DSS components not subject to <<ASCE 7>>​​​ special certification requirements. |
| DSS | Designated seismic system |
| h | Average roof height of structure with respect to the base |
| IBC | International Building Code |
| Ip | Component importance factor |
| LS | Limit state |
| Ra | Actual component response modification coefficient |
| RC | Risk category |
| Rp | Component response modification factor |
| SDB | Seismic design basis |
| SDC | Seismic Design Category |
| SDS | Design earthquake spectral response acceleration parameter at short period |
| SD1 | Design earthquake spectral response acceleration parameter at 1- second period |
| T0 | Period at which the peak of the Design Response Spectrum begins |
| Wp | Component operating weight |
| z | Height in structure of point of attachment of component with respect to the base (per <<ASCE 7>>)3 |

      - _______________

        - 3Per <<ICC-ES AC156>>, z = height of structure with respect to grade, at point of attachment of the component

      - ***************************************************************************************

      - Edit submittals to include only those absolutely necessary to assure the requirements and features that are important for the specific project will be met. Coordinate with Article Section Includes, PART 2 and PART 3.

      - ***************************************************************************************

ACTION SUBMITTALS

      - ***************************************************************************************

      - In what follows, “seismically qualified” means the component meets the seismic performance requirements specified in PART 2 of this Section.

      - For elements of the designated seismic system as defined in IBC Section 202, the special inspector shall verify that the component labeling, anchorage, and mounting conform to the Certificate of Compliance.

      - ***************************************************************************************

Qualification Testing: Provide documentation for component(s) qualified using the qualification testing method.

CoC certifying that the ​​​​<< list components or refer to appropriate table in PART 2>>​​​​ ​​​​<< is; or  are>>​​​​​ seismically qualified by qualification testing performed by​​​​<< manufacturer and witnessed by; or  None - N/A>>​​​​ a qualified testing agency.

        - ******************************************************************************

        - In accordance with IBC Section 1705.13.4 and ASCE 7 Section 13.2.2, submit a Certificate of Compliance (CoC) for Special-Certification Components (Designated Seismic Systems), along with evidence demonstrating compliance as required by ASCE 7 Section 13.2.2. Accordingly, retain the following subparagraph.

        - ******************************************************************************

Evidence associated with CoC for Special-certification components:

Test Report per <<ICC-ES AC156>> Section 5.2, and including the content stipulated in the PART 3 Article herein, “LOADS ON SUPPORTING STRUCTURE.”

The appendix stipulated in <<ICC-ES AC156>> Section 5.2.2.9 shall be provided with the Test Report.

      - ***************************************************************************************

      - The following paragraph should be retained under most circumstances (i.e., unless it’s known that only qualification solely by testing will be necessary/applicable).

      - ASCE 7 13.2.2.1 doesn’t permit active equipment to be qualified by analysis; however, in all other instances, the intent of 13.2.1 & 13.2.2 is to allow flexibility in the performance of qualification.

      - If paragraph is not retained then edit subsequent portions of Section accordingly.

      - ***************************************************************************************

Qualification Analysis: Provide documentation for component(s) qualified using the qualification analysis method.

CoC certifying that the ​​​​​<< list components or refer to appropriate table in PART 2>>​​​​​ ​​​​​<< is; or  are>>​​​​​ seismically qualified by qualification analysis performed by​​​​​<< the manufacturer, or; or  None - N/A>>​​​​​​ a qualified professional engineer.

        - ******************************************************************************

        - In accordance with IBC Section 1705.13.4 and ASCE 7 Section 13.2.2, submit a Certificate of Compliance (CoC) for Special-Certification Components (Designated Seismic Systems), along with evidence demonstrating compliance as required by ASCE 7 Section 13.2.2. Accordingly, retain the following subparagraph.

        - ******************************************************************************

Evidence associated with CoC for Special-certification components:

Seismic Qualification Report (SQR) including all data, results and conclusions. The required content for the SQR is located in Attachment 1 herein.

      - **************************************************************************************

      - A combination of qualification methods should be used only when qualification solely by testing or solely by analysis is known or suspected to be inadequate. For example:

      - Qualification by testing supported by analysis is appropriate for subsystems of large or complex components (e.g., large chillers or skid-mounted equipment assemblies), where individual components may be qualified by testing while the overall structural frame is evaluated by analysis.

      - Qualification by analysis supported by testing is appropriate for systems that include primary components suitable for analytical qualification and subcomponents that are not adequately addressed by analysis alone and therefore require testing.

      - **************************************************************************************

Combination of Qualification Methods: Documentation for a component(s) qualified by a combination of qualification methods.

CoC certifying that the ​​​​​​<< list components or refer to appropriate table in PART 2>>​​​​​​ ​​​​​​<< is; or  are>>​​​​​​ seismically qualified by a combination of qualification methods performed by​​​​​​<< the manufacturer and witnessed by a qualified testing agency, or performed by; or  None - N/A>>​​​​​​ a qualified testing agency and​​​​​​<< /or; or  None - N/A>>​​​​​​ a qualified professional engineer​​​​​​<< , as applicable; or  None - N/A>>​​​​​​.

        - ******************************************************************************

        - In accordance with IBC Section 1705.13.4 and ASCE 7 Section 13.2.2, submit a Certificate of Compliance (CoC) for Special-Certification Components (Designated Seismic Systems), along with evidence demonstrating compliance as required by ASCE 7 Section 13.2.2. Accordingly, retain the following subparagraph.

        - ******************************************************************************

Evidence associated with CoC for Special-certification components:

Seismic Qualification Report (SQR) including all data, results and conclusions. The required content for the SQR is located in Attachment 1 herein.

      - **************************************************************************************

      - Retain the following paragraph if this Section is intended to ensure compliance with ASCE 7 Chapter 13 through Manufacturer’s Certification. When compliance is based on manufacturer’s certification, items must be installed per the manufacturer’s requirements. Evidence of compliance may be a signed statement from the manufacturer’s representative or a registered design professional confirming the component or system is seismically qualified.

      - If retained, revise to reflect project-specific details by inserting the applicable component into the brackets or use Table 1.1 for each distinct component type as needed. Provide corresponding qualification requirements under the applicable Article(s) in part 2.

      - If supporting evidence is required, add corresponding submittal requirements. Use ASCE 7, Commentary Section C13.2.1 to define acceptable testing and analysis documentation and revise the submittal requirements (including Attachment 1, if applicable) accordingly.

      - Compliance through manufacturer-provided documentation is typically suitable for noncritical systems (Ip = 1.0) or when the manufacturer has prequalified systems. This approach streamlines the process by relying on verified product data and testing rather than requiring project-specific seismic design and documentation.

      - ***************************************************************************************

Manufacturer's Certiﬁcation: Documentation for ​​​​​​​<< Click here to select component type(s) (e.g., noncritical, DOTS);  noncritical components;  DOTS; and  _______>>​​​​​​​ ​​​​​​​<< listed in Table 1.1;  shown on drawings; or  _______>>​​​​​​​, accessories, and subcomponents.

Manufacturer’s certiﬁcation that the component is seismically qualiﬁed: Indicate whether certification is based on actual test of assembled components, supports and attachments, or on calculation/analysis of them.

Dimensioned Outline Drawings of Component: Identify center of gravity and locate and describe mounting, supports and attachment provisions.

Specifications for, and drawings of, the component, supports and attachments as necessary to install component in a manner consistent with the certification shall be provided.

        - ******************************************************************************

        - Retain the following subparagraph if anchorage to concrete is required.

        - ******************************************************************************

Provide detailed description of anchorage products/devices on which the certification is based and their installation requirements.

The description must clearly indicate how the use of the products will result in compliance with the anchorage requirements of <<ACI CODE-318>>.

        - Table 1.1: Components Qualified via Manufacturer’s Certiﬁcation

| ID | Description |
| --- | --- |
| NC-1 |  |
| DOTS-1 |  |

        - ******************************************************************************

        - Retain the following subparagraph to request supporting evidence for Manufacturer's Certiﬁcation.

        - ******************************************************************************

Evidence associated with Manufacturer's Certiﬁcation:

An analysis report  derivation of the forces used for the design of the system, the derivation of displacements and reactions, and the design of the supports and anchorages.

A test report describing the test configuration, boundary conditions, instrumentation, loading protocol, and results.

An experience data report documenting prior performance under comparable seismic loading and installation conditions.

INFORMATIONAL SUBMITTALS

      - ***************************************************************************************

      - Edit the following paragraph to align with and support revisions made in the ACTION SUBMITTALS Article.

      - Since the intent of ASCE 7 13.2.1 & 13.2.2 is to allow flexibility in the performance of qualification, the paragraph should be retained “as is” under most circumstances.

      - If this paragraph is not retained as written, revise all related portions of the Section to maintain consistency.

      - If retained, coordinate paragraph with qualification requirements in Section ​<< 01 4000 - Quality Requirements - Non-Nuclear>>​  and as may be supplemented in "Quality Assurance" Article. Professional engineer is defined in Section ​<< 01 4000 - Quality Requirements - Non-Nuclear>>​.

      - ***************************************************************************************

Qualification Data: Submit credentials for the ​<< professional engineer; and  testing agency>>​, as applicable.

QUALITY ASSURANCE

      - ***************************************************************************************

      - NOTE: Select the option referencing AC156 in the following paragraph if qualification by testing apply to the Project.

      - ***************************************************************************************

All work shall be performed per Project Specification Section ​​​​<< 01 4000 - Quality Requirements - Non-Nuclear>>​​​​​​​​<< , and ICC-ES AC156 Section 5.1; or  None - N/A>>​​​​ as applicable.

PART 2 - PRODUCTS

QUALIFICATION REQUIREMENTS

Qualification shall be based on analysis or testing per <<ASCE 7>> Chapter 13, or a combination of analysis and testing per subsequent portions of this Section.

Qualification shall demonstrate that the component, and its support(s) and attachment(s), is capable of achieving the seismic performance requirement(s) indicated in the Article(s) below.

The data/input necessary to perform the qualification is provided in the Articles below.

The DBE is represented by, and/or shall be derived from, this data/input per <<ASCE 7>>.

      - ***************************************************************************************

      - The following three articles should be activated through the corresponding selections or choices in the PART 1 Article SECTION INCLUDES.

      - ***************************************************************************************

QUALIFICATION REQUIREMENTS FOR NONCRITICAL COMPONENTS

The qualification requirements for noncritical components are indicated in Tables 2.1(a) and 2.1(b).

      - *** OR ***

The qualification requirements for noncritical components are as shown on drawings.

      - ***************************************************************************************

      - For SDC-1 components, the options for the value of Ra are based on DOE-STD-1020-2016. Selection of the correct Ra value depends on the LS (from the SDB), the value of Rp (from ASCE 7 Ch. 13 Tables 13.5-1 and 13.6-1), and the following:

        - For LS A, Ra = Rp.

        - For LS B, Ra = Rp/1.25; however, Ra > 1.2, which means Ra = 0.8Rp for Rp > 1.5.

        - If/when Rp < 1.5, use Ra = 1.2 in lieu of 0.8Rp.

        - For LS C, Ra = Rp/1.5; however, Ra > 1.2, which means Ra = 0.67Rp for Rp > 1.8.

        - If/when Rp < 1.8, use Ra = 1.2 in lieu of 0.67Rp.

        - For LS D, Ra = 1.2.

      - ***************************************************************************************

The horizontal component of seismic load acting on an SDC-1 component shall be determined based on Ra (from <<DOE-STD-1020>>) in lieu of Rp (from <<ASCE 7>>).

      - ***************************************************************************************

      - Edit the following tables (i.e., add or remove rows) as needed/applicable to include all the noncritical component requiring qualification.

      - Edit the data in the middle columns (i.e., SDS –> IBC SDC) based on the project’s SDC: Select 1st option if SDC D applies; select 2nd option if SDC C applies.

      - The data in the last two columns of the following table is used to determine Fp using equation 13.3-4 rather than 13.3-1. where ai is the maximum acceleration at level i obtained in accordance with the analysis requirements of ASCE 7-16 Section 13.3.1.4. For example, use R = 1 when linear dynamic analysis procedures are applied to calculate the response of the structure housing the nonstructural component. If ai and Ax are not provided, delete these columns.

      - ***************************************************************************************

      - Table 2.1(a): Noncritical Components

| ID | Ip | Description |
| --- | --- | --- |
| NC-1 | 1.0 |  |
| NC-2 | 1.0 |  |

      - Table 2.1(b): Qualification Requirements for Noncritical Components

| Seismic Performance Requirement: Position retention following the DBE. |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ID | h (feet) | z (feet) | ap | LS | Rp, Ra | SDS (g) | SD1 (g) | T0 (sec) | IBC SDC | ai (g) | Ax |
| NC-1 |  |  |  |  |  | ​​ | ​​ | ​​ | ​​ |  |  |
| NC-2 |  |  |  |  |  |  |  |  |  |  |  |

QUALIFICATION REQUIREMENTS FOR SPECIAL-CERTIFICATION COMPONENTS

The qualification requirements for special-certification components are indicated in Tables 2.2(a) and 2.2(b).

      - *** OR ***

The qualification requirements for special-certification components are as shown on drawings.

      - ***************************************************************************************

      - For SDC-1 components, the options for the value of Ra are based on DOE-STD-1020-2016. Selection of the correct Ra value depends on the LS (from the SDB), the value of Rp (from ASCE 7 Ch. 13 Tables 13.5-1 & 13.6-1), and the following:

        - There’s no such thing as LS A for SDC-2 components.

        - For LS B, Ra = Rp.

        - For LS C, Ra = Rp/1.2; however, Ra > 1.2, which means Ra = 0.833Rp for Rp > 1.5.

        - If/when Rp < 1.5, use Ra = 1.2 in lieu of 0.833Rp.

        - For LS D, Ra = 1.2.

      - This author note also applies to the “Ra subpara.” in the next Article (i.e., Qual. Reqmts. for DOTS Components).

      - ***************************************************************************************

The horizontal component of seismic load acting on an SDC-2 component shall be determined based on Ra (from <<DOE-STD-1020>>) in lieu of Rp (from <<ASCE 7>>).

      - ***************************************************************************************

      - Edit the following tables (i.e., add or remove rows) as needed/applicable to include all the DSS requiring qualification

      - Per the author note in PART 1 associated with the DEFINITION of “Seismic performance requirements,” for nuclear special-certification components, what’s required by “functional/ operable” must be defined/explained (i.e., unless LS D applies).

      - Edit the data in the middle columns (i.e., SDS –> IBC SDC) based on the project’s SDC: Select 1st option if SDC D applies; select 2nd option if SDC C applies.

      - The data in the last two columns of the following table is used to determine Fp using equation 13.3-4 rather than 13.3-1. where ai is the maximum acceleration at level i obtained in accordance with the analysis requirements of ASCE 7-16 Section 13.3.1.4. For example, use R = 1 when linear dynamic analysis procedures are applied to calculate the response of the structure housing the nonstructural component. If ai and Ax are not provided, delete these columns.

      - Note: Per ASCE 7-16 Section 13.2.2, certification of DSS components through analysis shall be limited to nonactive components and shall be based on seismic demand considering Rp/lp equal to 1.0

      - ***************************************************************************************

      - Table 2.2(a): Designated Seismic Systems

| ID | Ip | Description (Purpose/Functional/Operable) |
| --- | --- | --- |
| DSS-1 | 1.5 |  |
| DSS-2 | 1.5 |  |

      - Table 2.2(b): Qualification Requirements for Designated Seismic Systems

| Seismic Performance Requirement: Position retention and functional/operable following the DBE. |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ID | h (feet) | z (feet) | ap | LS | Rp, Ra | SDS (g) | SD1 (g) | T0 (sec) | IBC SDC | ai (g) | Ax |
| DSS-1 |  |  |  |  |  | ​​ | ​​ | ​​ | ​​ |  |  |
| DSS-2 |  |  |  |  |  |  |  |  |  |  |  |

QUALIFICATION REQUIREMENTS FOR DOTS COMPONENTS

The qualification requirements for DOTS Components are indicated in Tables 2.3(a) and 2.3(b).

      - *** OR ***

The qualification requirements for DOTS Components are as shown on drawings.

The horizontal component of seismic load acting on an SDC-2 component shall be determined based on Ra (from <<DOE-STD-1020>>) in lieu of Rp (from <<ASCE 7>>).

      - ***************************************************************************************

      - Edit the following tables (i.e., add or remove rows) as needed/applicable to include all the DOT requiring qualification.

      - Per the author notes in PART 1 associated with the DEFINITION of “Seismic performance requirements,” for non-nuclear and nuclear DOTS components, what’s required by “functional/ operable” must be defined/explained (i.e., for other than LS D components).

      - Edit the data in the middle columns (i.e., SDS –> IBC SDC) based on the project’s SDC: Select 1st option if SDC D applies; select 2nd option if SDC C applies.

      - The data in the last two columns of the following table is used to determine Fp using equation 13.3-4 rather than 13.3-1. where ai is the maximum acceleration at level i obtained in accordance with the analysis requirements of ASCE 7-16 Section 13.3.1.4. For example, use R = 1 when linear dynamic analysis procedures are applied to calculate the response of the structure housing the nonstructural component. If ai and Ax are not provided, delete these columns.

      - Note: Per ASCE 7-16 Section 13.2.2, certification of DSS components through analysis shall be limited to nonactive components and shall be based on seismic demand considering Rp/lp equal to 1.0

      - ***************************************************************************************

      - Table 2.3(a): DSS other than Special-certification Components

| ID | Ip | Description (Purpose/Functional/Operable) |
| --- | --- | --- |
| DOT-1 | 1.5 |  |
| DOT-2 | 1.5 |  |

      - Table 2.3(b): Qualification Requirements for DSS other than Special-certification Components

| Seismic Performance Requirement: Position retention and functional/operable following the DBE. |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| ID | h (feet) | z (feet) | ap | LS | Rp, Ra | SDS (g) | SD1 (g) | T0 (sec) | IBC SDC | ai (g) | Ax |
| DOT-1 |  |  |  |  |  | ​​ | ​​ | ​​ | ​​ |  |  |
| DOT-2 |  |  |  |  |  |  |  |  |  |  |  |

      - ***************************************************************************************

      - Include PART 3 if applicable to project (i.e., for projects using testing or analysis qualification methods.

      - ***************************************************************************************

PART 3 - EXECUTION

QUALIFICATION METHODS

The seismic qualification of a component, to include its support(s) and attachment(s), is achieved by demonstrating it is capable of achieving its seismic performance requirement when subjected to the DBE. Regardless of the qualification program(s) chosen, the applicable seismic performance requirements are as stated in the applicable table in PART 2 (herein). The Subcontractor responsible for this Section may select one of the following qualification methods:

Qualification testing.

Qualification analysis.

A combination of the aforementioned testing and analysis, for which there are two options:

Qualification testing supported by analysis.

Qualification analyses supported by testing.

Qualification Testing

The use of the qualification-testing method solely is appropriate when at least one of the following conditions apply:

The component is a noncritical component.

The component is a special-certification component.4

The component is a DOTS component.

The structural configuration of the component is extremely complex and/or beyond the capability of mathematical modeling techniques.

The response of the component is expected to be significantly nonlinear.

        - _______________

        - 4Shake table testing is required by <<ASCE 7>> for the qualification of active parts or energized components of special certification components that are active mechanical and electrical equipment.

Qualification Analysis

        - ******************************************************************************

        - Note: Per ASCE 7-16 Section 13.2.2, certification of DSS components through analysis shall be limited to nonactive components and shall be based on seismic demand considering Rp/lp equal to 1.0

        - ******************************************************************************

The use of the qualification-analysis method solely is appropriate when at least one of the following conditions apply:

The component is a noncritical component.

The component is a special-certification component with hazardous substances.

The component is a DOTS component.

The structural configuration of the component is simple and/or within the capability of mathematical modeling techniques.

The response of the component is expected to be linear or exhibit simple nonlinear behavior.

The effect of attached components and the superposition of load conditions are too complex for testing.

The use of the qualification-analysis method for active parts or energized components of special-certification components that are active mechanical and electrical equipment is not permitted.

When the qualification-analysis method is used, any/all assumptions must be documented and justified.

Qualification testing supported by analysis

This method should be considered only when it is known/suspected that qualification solely by testing, or solely by analysis, is inadequate.

The use of qualification testing supported by analysis is appropriate when at least one of the following conditions apply:

The component is a noncritical component.

The component is a special-certification component.

The component is a DOTS component.

The component is too large to be qualified by solely by shake-table testing, thereby requiring a subsystem approach.

Subsystems of large, complex components (e.g., large chillers, skid-mounted equipment assemblies) may be qualified individually by testing, while the overall structural frame can be evaluated by analysis.

This approach is not applicable if the influence of the frame on the input to the tested component(s) or subsystem(s) cannot be adequately accounted for.

Qualification analysis supported by testing.

This method should be considered only when it is known/suspected that qualification solely by testing, or solely by analysis, is inadequate.

The use of qualification analysis supported by testing is appropriate when at least one of the following conditions apply:

The component is a noncritical component.

The component is a special-certification component.

The component is a DOTS component.

Supporting tests may be used as follows:

To determine the deflection limits within which functionality/ operability is maintained (if not provided by the equipment manufacturer).

To determine the dynamic parameters needed for constructing or verifying mathematical models.

To determine the assumptions to be used in the analysis.

To determine the amount of nonlinear response involved.

      - ***************************************************************************************

      - The following four Articles are designer options based on project-specific requirements. These Articles are automatically activated by the selections made in PART 2, Article ACTION SUBMITAL PART 3, Article QUALIFICATION METHODS. Retain only the Articles applicable to the selected qualification method(s).

      - ***************************************************************************************

QUALIFICATION TESTING

      - ***************************************************************************************

      - The next paragraph can be edited if qualification of active components is not applicable, or if an alternative to “AC156” has been agreed on. Refer to the “AC156 author note” in PART 1 under REFERENCES.

      - ***************************************************************************************

Qualification testing of all components shall be per <<ASCE 7>> Section 13.2.5 and the following:

Shake-table testing shall be done per <<ICC-ES AC156>>.

Shake-table testing is mandatory for active parts or energized subcomponents of the following components:

Special-certification components that are active mechanical or electrical equipment.

          - **********************************************************************

          - Include the following subparagraph if applicable to project.

          - **********************************************************************

Special-certification components with hazardous substances

If the component being qualified is connected to other components (in service), the qualification shall provide the permissible forces (e.g., nozzle loads, etc.) and, as applicable, anticipated displacements of the component at the connection points to facilitate assessment for consequential damage, in accordance with <<ASCE 7>> Section 13.2.3.

QUALIFICATION ANALYSIS

      - ***************************************************************************************

      - NOTE: Unlike testing, ASCE 7 is silent regarding how analyses are to be done, what they have to be in accordance with, etc. Therefore, it is reasonable to assume that any analysis technique/tool is fine as long as it’s consistent with conventional/accepted engineering practices, and its rigor is commensurate with the task at hand. The 1st three paragraphs below are based on this assumption.

      - ***************************************************************************************

Qualification analysis of noncritical and DOTS Components shall be, at a minimum, a linear, static, 2-D analysis, and shall include the demands stipulated in <<ASCE 7>> Chapter 13.

Qualification analysis of special-certification components shall be of adequate rigor such that the seismic performance requirement (e.g., containment of contents following the DBE, etc.) is demonstrated/proven, and shall include the demands stipulated in <<ASCE 7>> Chapter 13.

The mathematical model used in qualification analyses shall include the “in-service” connectivity (to other components), support and attachment as applicable, and nonlinear models shall be used for all elements not responding linearly to the DBE.

One of the stipulated demands in <<ASCE 7>> Chapter 13 is “service loads associated with the component.” For use herein, the following “service loads” shall be included, or otherwise accounted for:

All loads resulting from the use of the component (e.g., operating loads for equipment, torque due to rotating parts, vibratory loads due to eccentricities, etc.), and from induced displacements by the supporting structure.

Capacity

The limiting strength(s) used in the analysis shall be per the <<ICC (IBC)>>  and the standards referenced therein.

The limiting deflection(s)/displacement(s) used in the analysis shall be those maximum deflections that won’t preclude the component from meeting its seismic performance requirement.

The use of deflection/displacement limits either provided by the component manufacturer or determined from supporting tests is acceptable.

Acceptability is based on the applicable demands (e.g., resultant stresses, deflections, etc.) not exceeding the associated capacities.

Any deviation from this requirement shall be justified in terms of the component achieving its seismic performance requirement.

If the component being qualified can/will be connected to other components, the qualification shall provide the permissible forces (e.g., nozzle loads, etc.) and, as applicable, anticipated displacements of the component at the connection points to facilitate assessment for consequential damage, in accordance with <<ASCE 7>> Section 13.2.3.

ANALYSIS SUPPORTING QUALIFICATION TESTING

Supporting analysis/analytical calculations may be used to develop data for use in qualification testing.

TESTS SUPPORTING QUALIFICATION ANALYSIS

Supporting tests may be either static or dynamic in nature; however, static tests aren’t applicable to the active parts, or the energized subcomponents, of active components.

Static supporting tests are conducted by applying static forces on the equipment. Typical data obtained from these tests are as follows:

Static deflections and flexibility parameters that are needed for constructing a mathematical model.

Distortion in the equipment casing, due to nozzle loads, and the deformation limits within which the equipment would maintain its operability/functionality.

Dynamic supporting tests shall be conducted using a shake table. Typical data obtained from dynamic supporting tests are as follows

Dynamic characteristics of the equipment (natural frequencies, mode shapes and damping factors).

Cross-coupling effects, i.e., the response in any direction due to the excitation in any other direction (in situations where installing accelerometers in some locations is impractical, cross-coupling may be estimated based on the response of the available accelerometer locations).

The significance of the response of the equipment to vibratory motion to determine the necessity of combining equipment nozzle loads with other dynamic loads.

LOADS ON SUPPORTING STRUCTURE

All loads transmitted by the component to the supporting structure shall be provided. The following loads, as applicable, shall be reported individually, and included in the determination of the transmitted loads.

Dead load/operating weight.

Operational/service loads.

Nozzle loads.

Pressure and thermal loads.

Additional loads due to seismic excitations.

Any other loads that are required to be transmitted to the structure/ foundation during the DBE.

​<< END OF MAIN SECTION;; or  END OF SECTION>>​ ​<< ATTACHMENT FOLLOWS; or  None - N/A>>​

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 01 8734, REV. 2, DATED APRIL 15, 2026.

    - **********************************************************************************************

      - If only Qualification Testing per ICC-ES AC156 is applicable, this Attachment is N/A.

      - If only Qualification Analysis is applicable, the testing-related portions of this attachment are N/A. Under all other circumstances, the entirety of this attachment is applicable and must be retained.

    - **********************************************************************************************

ATTACHMENT 1

    - MINIMUM CONTENT FOR SEISMIC QUALIFICATION REPORTS

    - I - TITLE PAGE

      - Include the following information on the Title Page:

Client

Supplier and Component Name.

Specification Package Number/Identification.

Revision Number.

Date.

    - II - General

      - This section shall include a description of the component, its function and the method of qualification used to verify this function. In addition, the following information must be given:

Project and owner names.

Specification and purchase order numbers.

Component Name and Identification/number.

Organization(s) performing qualification programs.

    - III - Data and Assumptions

      - Testing Section: The following data shall be included:

Type of testing machine.

Loads considered and simulated during the test.

Methods used to simulate the supporting structure, details of the attachment to the supporting structure and/or testing machine.

Position and orientation of setting component (photographs are recommended).

Steps taken to monitor the function of component during the test and accelerometer locations and orientations (photographs are recommended).

6) Means of generating test response spectra (if applicable).

Analytical Section: The following data shall be presented:

Loads considered.

Damping values used in the analysis.

Codes and standards used as bases for the analysis.

Assumptions and engineering judgements made for idealizing boundary conditions, converting the load criteria to actual loads used for analyses/ calculations and converting the design criteria to actual stress, deformation and stability limits. Justification shall be provided for all assumptions and engineering judgements used.

A list of the computer programs and software revision numbers, to keep track of V&V, used in the analysis and the documentation which establish the validity of any computer program used, if not included in the public domain.

    - IV - Qualification Procedure

      - Testing Section: State type of test, wave form, frequency intervals and range, acceleration levels, axes of excitation, phase between inputs monitoring set-up and any other data to completely describe the input  motion and show it is applied.

Analytical Section: State the method used in the analysis, mathematical equations and their derivation from basic principles including appropriate references.

    - V - Results

      - Testing Section: This section shall include the measurements obtained from the test and their interpretations. Findings and observations from monitoring the function of the component and/or inspection shall be presented. All results shall be presented in either numerical or graphical form.

Analytical Section: Show actual design calculations and sketches for the mathematical models, including numbering used for the node points and numbers. If possible, show loads, resultant forces, moments, stresses and deformations on the mathematical model of the component.

    - VI – Supporting-Structure Loads

      - The loads transmitted by the component to the supporting structure, calculated in the previous section, shall be presented in this section.

    - VII - Conclusions

      - Give a brief summary of the results obtained from the qualification program. A concise statement of the conclusion reached, which should satisfy the qualification requirements, shall be stated in this section.

    - VIII – Drawings and Specifications

      - Submit dimensioned outline drawings of component. Identify center of gravity and locate and describe mounting and attachment provisions.

Submit drawings of, and specifications for, the component, supports and attachments as necessary to install component in a manner consistent with the certification shall be provided.

If anchorage to concrete applies to component attachment, provide detailed description of anchorage products/devices on which the certification is based and their installation requirements.

Description must clearly indicate how the use of the products will result in compliance with the anchorage requirements of <<ACI CODE-318>>.

END OF SECTION