Section 03 3001 
Reinforced Concrete

  - ************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 20 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., SECTION INCLUDES in PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Structural POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable sections from all Divisions specifically Division 1, General Requirements.

      - This Section applies to non-prestressed1 structural concrete for buildings that are designed in accordance with ACI 318, facilities classified as Natural Phenomena Hazards (NPH) Risk Category (RC) I - IV facilities, and ML-3 and ML-4 projects1. In general, this section does not apply to nuclear facilities. This section can be used for Safety Significant (SS) nuclear SSCs that are classified as NDC-1 or NDC-2 (i.e., designed and constructed as though they are RC II or RC IV, respectively, per LANL ESM Chapter 5 - Structural, Section III).2 If this section is used for ML-1 or ML-2 concrete, all applicable quality-related requirements from Section ​​​<< 03 3021 - Reinforced Concrete - High Confidence>>​​​ must be incorporated.

      - ==========================================================

      - This template is developed based on ACI 301-20 and ACI 318-19. The specifier shall update this section based on the code of record adopted by the project, if differing from the ACI editions referenced above.

      - Steel-fiber-reinforced concrete: in this instance, the LANL pre-approved mix designs can’t be used since they do not include steel fiber(s).

      - Lightweight Structural Concrete: in this instance, the LANL pre-approved mix designs can’t be used since they are ‘normal weight.’ ACI 318 Ch 26 includes requirements for ‘lightweight mixes (that are not included in ACI 301).’

      - Mass Concrete (ref. LANL ESM Chapter 5 - Structural, Section II.4.2).

      - Shrinkage-Compensating Concrete: in this instance, the LANL pre-approved mix designs can’t be used since they don’t meet the “Materials” and “Performance and design requirements” stipulated in ACI 301.

      - Industrial Floor Slabs.

      - Precast structural concrete: this Section does not apply to such work and can’t be altered for such.  LANL Section << 03 4100 - Precast Structural Concrete>>, must be used.

      - Similarly, this Section does not apply to work involving post-tensioned concrete, precast and cast-in-place architectural concrete, and tilt-up construction; and cannot be altered for such. SpecLink templates may be used for these types of work.

      - The LANL ESM Chapter 5 - Structural, Section I ‘crosswalk tables’ between the old NPH Performance Category designations (i.e., PC-1 – PC-3) and the current designations (i.e., RCs and NDCs) should be reviewed by those using this section for work in existing facilities (that are still ‘PC-based’).

      - _________________________

      - 1 While this Section does not apply to work involving pretensioned concrete, it can be altered for such by adding the applicable provisions, requirements, and submittals, per ACI 318 and 301. The same applies for the following types of work:

      - 2 For nuclear facilities and their safety class (SC) structures, systems, and components (SSCs), use Section ​<< 03 3021 - Reinforced Concrete - High Confidence>>​, which applies to concrete structures designed per , facilities classified as NPH Design Category (NDC)-3, and ML-1/SC SSCs. For safety significant (SS) SSCs, DOE Order 420.1C may require the use of ACI 349 (hence, follow Section ); however, LANL ESM Chapter 5 - Structural, Section III.2.1.A.4 provides some flexibility on this regard.

      - 3 While the vast majority of "structural-concrete projects" are "Building-Related" and thus have designs based on ACI 318, there are instances where this paradigm does not hold. For example, a slab-on-grade that does not transmit vertical loads or lateral forces from other portions of the structure to the soil is still "structural concrete" if it is designed to resist gravity loads (e.g. industrial floors designed in accordance with ACI 360R, etc.). Where an outside slab or pad is not IBC work or designed per ACI 360R, this template can be used to create a section for miscellaneous but reinforced concrete with less rigorous inspection.

  - ************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

      - ***************************************************************************************

      - Retain the applicable paragraphs from the following.

      - ***************************************************************************************

Formwork, shoring, bracing, and anchorage.

Reinforcement and accessories.

Cast-in-place, normal weight, non-prestressed concrete.

Construction, isolation, and contraction joint devices associated with concrete work.

RELATED REQUIREMENTS

Section << 01 3300 - Submittal Procedures>>.

Section << 01 4000 - Quality Requirements - Non-Nuclear>>.

Section << 01 4216 - Definitions>>.

Section << 01 4444 - Offsite Welding, Brazing and Joining Requirements>>.

Section << 01 4455 - Onsite Welding, Brazing and Joining Requirements>>.

Section << 01 4525 - Non-Destructive Examination (NDE) Requirements>>.

Section << 01 8113.13 - Sustainable Design>>.

Section << 03 6000 - Grouting>>.

      - ***************************************************************************************

      - References noted in this Section form a part of the Section to the extent applicable. The publications are referred to in the text by the basic designation only.

      - Codes and Standards: The following list provide the codes and standards that shall be used and referenced for this Project.

      - Notes:

      - (1) The applicable edition/version of a given code or standard shall be either its latest or the version referenced by the edition of ACI 318 that applies to the Project.

      - (2) Codes and Standards that are referenced within the codes and standards tabulated below shall be considered applicable to this Project.

      - ***************************************************************************************

REFERENCE STANDARDS

ACI CODE-318 - Building Code for Structural Concrete—Code Requirements and Commentary.

ACI PRC-201.2 - Durable Concrete—Guide.

ACI PRC-302.1 - Guide to Concrete Floor and Slab Construction.

ACI PRC-304 - Guide for Measuring, Mixing, Transporting, and Placing Concrete.

ACI PRC-304.2 - Guide to Placing Concrete by Pumping Methods.

ACI PRC-304.4 - Placing Concrete with Belt Conveyors.

ACI PRC-305 - Guide to Hot Weather Concreting.

ACI PRC-306 - Guide to Cold Weather Concreting.

ACI PRC-308 - Guide to External Curing of Concrete.

ACI PRC-309 - Guide for Consolidation of Concrete.

ACI PRC-347 - Guide to Formwork for Concrete.

ACI SPEC-117 - Specification for Tolerances for Concrete Construction and Materials.

ACI SPEC-301 - Specifications for Concrete Construction.

ACI SPEC-311.6 - Specification for Testing Ready-Mixed Concrete.

APA PS 1 - Structural Plywood.

ASTM A615/A615M - Standard Specification for Deformed and Plain Carbon-Steel Bars for Concrete Reinforcement.

ASTM A706/A706M - Standard Specification for Deformed and Plain Low-Alloy Steel Bars for Concrete Reinforcement.

ASTM A970 - Standard Specification for Headed Steel Bars for Concrete Reinforcement.

ASTM A1064/A1064M - Standard Specification for Carbon-Steel Wire and Welded Wire Reinforcement, Plain and Deformed, for Concrete.

ASTM C31/C31M - Standard Practice for Making and Curing Concrete Test Specimens in the Field.

ASTM C33/C33M - Standard Specification for Concrete Aggregates.

ASTM C39/C39M - Standard Test Method for Compressive Strength of Cylindrical Concrete Specimens.

ASTM C42 - Standard Test Method for Obtaining and Testing Drilled Cores and Sawed Beams of Concrete.

ASTM C94/C94M - Standard Specification for Ready-Mixed Concrete.

ASTM C138/C138M - Standard Test Method for Density (Unit Weight), Yield, and Air Content (Gravimetric) of Concrete.

ASTM C143/C143M - Standard Test Method for Slump of Hydraulic-Cement Concrete.

ASTM C150/C150M - Standard Specification for Portland Cement.

ASTM C171 - Standard Specification for Sheet Materials for Curing Concrete.

ASTM C172/C172M - Standard Practice for Sampling Freshly Mixed Concrete.

ASTM C231/C231M - Standard Test Method for Air Content of Freshly Mixed Concrete by the Pressure Method.

ASTM C260/C260M - Standard Specification for Air-Entraining Admixtures for Concrete.

ASTM C309 - Standard Specification for Liquid Membrane-Forming Compounds for Curing Concrete.

ASTM C457 - Standard Test Method for Microscopical Determination of Parameters of the Air-Void System in Hardened Concrete.

ASTM C494/C494M - Standard Specification for Chemical Admixtures for Concrete.

ASTM C595/C595M - Standard Specification for Blended Hydraulic Cements.

ASTM C618 - Standard Specification for Coal Ash and Raw or Calcined Natural Pozzolan for Use in Concrete.

ASTM C1059/C1059M - Standard Specification for Latex Agents for Bonding Fresh to Hardened Concrete.

ASTM C1064/1064M - Standard Test Method for Temperature of Freshly Mixed Hydraulic-Cement Concrete.

ASTM C1077 - Standard Practice for Agencies Testing Concrete and Concrete Aggregates for Use in Construction and Criteria for Testing Agency Evaluation.

ASTM C1157/C1157M - Standard Performance Specification for Hydraulic Cement.

ASTM C1260 - Standard Test Method for Potential Alkali Reactivity of Aggregates (Mortar-Bar Method).

ASTM C1315 - Standard Specification for Liquid Membrane-Forming Compounds Having Special Properties for Curing and Sealing Concrete.

ASTM C1567 - Standard Test Method for Determining the Potential Alkali-Silica Reactivity of Combinations of Cementitious Materials and Aggregate (Accelerated Mortar-Bar Method).

ASTM C1602/C1602M - Standard Specification for Mixing Water Used in the Production of Hydraulic Cement Concrete.

ASTM D1751 - Standard Specification for Preformed Expansion Joint Filler for Concrete Paving and Structural Construction (Nonextruding and Resilient Asphalt Types).

ASTM D3963/D3963M - Standard Specification for Fabrication and Jobsite Handling of Epoxy-Coated Steel Reinforcing Bars.

ASTM E96 - Standard Test Methods for Water Vapor Transmission of Materials.

ASTM E329 - Standard Specification for Agencies Engaged in Construction Inspection, Testing, or Special Inspection.

ASTM E1155/E1155M - Standard Test Method for Determining FF Floor Flatness and FL Floor Levelness Numbers.

ASTM E1745 - Standard Specification for Plastic Water Vapor Retarders Used in Contact with Soil or Granular Fill under Concrete Slabs.

AWS D1.4/D1.4M - Structural Welding Code - Steel Reinforcing Bars.

CPA A135.4 - Basic Hardboard.

CRSI - RB4.1 - Supports for Reinforcement Used in Concrete.

CRSI (P1) - Placing Reinforcing Bars, 10th Edition.

ICC (IBC) - International Building Code.

DEFINITIONS

The terms and acronyms used in this specification are defined in Sections << 01 4000 - Quality Requirements - Non-Nuclear>> and << 01 4216 - Definitions>>, and COE Glossary of Terms, except for those defined below.

Cementitious Material:  Portland cement by itself, or Portland cement in combination with natural pozzolan (or fly ash, silica fume, and slag cement).

National Institute of Standards and Testing: NIST.

Plain Concrete: Structural concrete with no reinforcement, or with no more than the minimum amount specified in <<ACI CODE-318>> for plain concrete.

Reinforced Concrete: Structural concrete reinforced with no less than the minimum amounts of reinforcement specified in <<ACI CODE-318>> (with the exception of Chapter 14).

Reinforcement:  Non-prestressed bars and wires; structural steel, pipe and tubing for composite columns; and headed shear studs and stud assemblies.

SUBMITTALS

All submittals require EOR review and notice to proceed. Where indicated in the log with Section ​​<< 01 3300 - Submittal Procedures>>​​, EOR review must occur prior to submission to LANL.

The Subcontractor is responsible for compliance with this Article and applicable provisions of <<ACI SPEC-301>>.

Submit submittals to the LANL STR within the specified time frames. The Subcontract or the LANL STR may adjust the time frames for the Project.

Retain all submittals and review comments (from LANL and/or EOR) in file for future reference during the Work.

In addition to the submittal requirements listed below, comply with submittal requirements shown on the Construction Drawings.

If a conflict exists between the requirements listed below and those shown on the Construction Drawings, notify the LANL STR.

      - ***************************************************************************************

      - Retain the following paragraphs and applicable subparagraphs, as required by the project.

      - Source: ACI 301-20 provides the requirement or submittal source unless noted otherwise. Refer to the cited Section for details on submittal items.

      - ***************************************************************************************

Submit the items listed below to LANL. Submit additional items required by codes, standards, or the Engineer of Record (EOR).

        - ******************************************************************************

        - Review the submittals listed in this subparagraph. Omit items that are not required. Document the rationale for each deletion.

        - ******************************************************************************

General requirements

          - ****The Quality Control Plan is only required when specified in Exhibit H of the Subcontract. Source: ACI 301 Section 1.5.3****

Subcontractor’s Quality Control Plan. One (1) month before initial placement.

          - ****The submittal required by ACI 301 Section 1.7.2.1 is “informally embedded” in this submittal. However, in the event that the constructor chooses to use a “currently-approved agency,” neither this submittal nor the ‘ACI 301’ one is necessary. Source [PART 1 Article QUALITY ASSURANCE] ****

Request to use a testing agency that is not currently approved by LANL. Three (3) months before initial placement.

          - ________________________

          - NOTE 1:  Submittal also applies to sub-tier concrete fabricators and batch plants.

          - NOTE 2:  Request must be approved before such agency can be used.

          - ****Source: ACI 301 Section 1.7.2.2(d)****

Test data on concrete mix materials and concrete mixtures. One (1) month before initial placement.

          - **** Except in the case of subcontracted design-build subcontracts, not required for concrete materials and mixtures when pre-approved mix designs are used for construction, unless specified in Exhibit H of the Subcontract. When required, refer to the NRMCA publication Guideline Manual for Quality Assurance and Quality Control for a description of suitable quality control program. Source: ACI 301 Section 1.7.2.2(e) ****

Quality control program of the concrete supplier. One (1) month before initial placement

        - ******************************************************************************

        - Review the submittals listed in this subparagraph. Omit items that are not required. Document the rationale for each deletion.

        - Submittal items under ACI 301 Sections 2.1.2.1 and 2.1.2.2 pertaining to formwork drawings, design calculations, etc. have been unnecessarily included on many LANL projects. When considering these items for inclusion on a project, in addition to guidance in the author note (e.g., ACI 347), the following should be carefully considered:  If the formwork were to fail, could safety be jeopardized, an injury result, costly damage occur, etc.?

        - ******************************************************************************

Formwork and formwork accessories

          - ****Refer to ACI 347R and ACI 347.2R for guidance on items to consider. Source: ACI 301 Section 2.1.2.1(d).****

Drawings and procedures for installation and removal of reshoring and backshoring. One and a half (1.5) months before formwork installation.

          - ****Source: ACI 301 Sections 2.1.2.1(e), 2.1.2.1 (f) and PART 2 Article FORM MATERIALS AND ACCESSORIES****

Product data on formwork release agent or formwork liners. 15 work days before formwork installation.

          - ****Source:  2.1.2.2(a)****

Shop drawings for formwork, shoring, reshoring and backshoring. 15 work days before formwork installation.

          - ****Source: ACI 301 Section 2.1.2.2(b)****

Design calculations for formwork, shoring, reshoring, and backshoring. 15 work days before formwork installation.

          - ****Source: ACI 301 Section 2.1.2.2(c)****

Data sheet on form ties. 15 work days before formwork installation.

          - ****Source: ACI 301 Section 2.1.2.2(d)****

Data sheet on isolation/expansion joint materials. 15 work days before formwork installation.

          - ****Source: ACI 301 Sections 2.1.2.2(e), and PART 2 Article FORM MATERIALS AND ACCESSORIES****

Data sheet on waterstop materials and splices. CoC from manufacturer that waterstops meet specified requirements.

          - ****Source: ACI 301 Sections 2.1.2.2(e), and PART 2 Article FORM MATERIALS AND ACCESSORIES****

CoC from manufacturer that waterstops meet specified requirements. 15 work days before formwork installation..

        - ******************************************************************************

        - Review the submittals listed in this subparagraph. Omit items that are not required. Document the rationale for each deletion.

        - ******************************************************************************

Reinforcement and reinforcement supports

          - ****Source: ACI 301 Section 3.1.2.1(a), & PART 1 Article QUALITY ASSURANCE****

CMTRs for each delivery traceable to the bundle tags by heat (or lot) number; and the respective, associated tags. Upon receipt of delivery.

          - ****Source: ACI 301 Section 3.1.2.1(b)****

Placing drawings showing fabrication dimensions and locations for placement of reinforcement and supports.1 month before reinforcement placement.

          - ****Source: ACI 301 Section 3.1.2.1(c)****

List of splices indicated in Subcontract Documents.1 month before reinforcement placement.

          - ****Source: ACI 301 Section 3.1.2.1(d)****

ICC-ESR report for mechanical splices. Demonstrate compliance with this Section and <<ACI CODE-318>>.

          - ****Source: ACI 301 Section 3.1.2.1(g)****

Copy of CRSI Epoxy Coating Plant Certification if epoxy-coated steel reinforcement is specified.15 work days before planned shipment date.

        - ******************************************************************************

        - Review the submittals listed in this subparagraph. Omit items that are not required. Document the rationale for each deletion.

        - ******************************************************************************

Concrete mixtures (Pre-approved and Alternate Mix Designs)

          - ****The following submittal is applicable only for ML-1 or ML-2 concrete. Source: PART 2 Article CONCRETE MIX********

Test report(s) indicating aggregate correction factor (determined per <<ASTM C231/C231M>>). Prior to first concrete placement

          - ****Source: 4.3.2, and ASTM C94-23, 14.1****

Provide a delivery ticket for each batch of concrete at the end of each day of placement. Ensure the ticket is legible. Comply with <<ASTM C94/C94M>> Section 14.1, with the following modifications and exceptions:

14.1.7:  Mix ID, name or designation of the concrete in conformance with that employed in job specifications.

14.2.2:  Cement type, brand, and amount.

14.2.3: Class, brand and amount of fly ash or natural pozzolans

14.2.4– 14.2.8:  Delete/Not necessary.

14.2.9: Type/brand and amount of admixtures

14.2.10, 14.2.15:  Delete/Not necessary.

Provide the following additional information:

Water-cementitious material ratio (w/cm).

Maximum amount of water permitted at the jobsite without exceeding the specified w/cm.

Water added at the jobsite

Add water at the jobsite only in the presence of a LANL technical representative, such as a field engineer or inspector.

          - ****Source: <<ACI SPEC-311.6>>, 3.2.1****

Compressive strength tests reports. Biweekly

          - ****Source: <<ACI SPEC-311.6>>, 3.2.1****

Fresh concrete test report (slump, temperature, air content, density (unit weight) etc.). Biweekly

        - ******************************************************************************

        - Review the submittals listed in this subparagraph. Omit items that are not required. Document the rationale for each deletion.

        - If only a pre-approved mix(es) is/are used on/by the Project, the submittals included below (i.e., Alternate Mix Designs) need not be submitted to LANL for review.

        - ******************************************************************************

Alternative Mix Designs

          - **********************************************************************

          - Check that mixture proportions conform to the requirements of PART 2 Article CONCRETE MIX for cementitious material content, w/cm, slump, nominal maximum size of coarse aggregate, air content, admixtures, and chloride-ion concentration, as well as compressive strength. In case of conflict with PART 2 Article CONCRETE MIX, contact LANL STR.

          - For guidance reviewing concrete mix design refer to GUIDELINES FOR REVIEWING CONCRETE MIX DESIGNS In Accordance with the 2019 CBC, prepared by SEAONC Construction Quality Assurance Committee (October 2019).

          - Source: PART 2 Article CONCRETE MIX, and ACI 318-19, 26.4.3.1(d)

          - **********************************************************************

Mixture proportions and characteristics. If different mixtures are to be used for different portions of proposed Work, CoC confirming that each mixture complies with the indicated mixture requirements. 15 work days before placement

          - **********************************************************************

          - Several different methods can be used to select mixture proportions that will produce the necessary placeability, density, strength, and durability of the concrete.

          - Field experience of concrete mixtures previously used under similar conditions provides the best assurance that the proposed concrete mixture can be used satisfactorily and will have the specified properties.

          - If no field test records are available, refer to ACI 211.1 for selecting the initial quantities of materials based on material properties and specified concrete properties. ACI 211.1 recommends mixture characteristics be checked by trial batches in the laboratory or in the field.

          - Source: PART 2 Article CONCRETE MIX, and ACI 318-19, 26.4.3.1(b)

          - **********************************************************************

Mixture strength data. Strength test records shall be < 2-years old. 15 work days before placement.

          - ****Source: PART 2 Article CONCRETE MIX, and ACI 318-19 26.4.1****

Information on types, classes, producers’ names, plant locations, and CoCs for cementitious materials; types, pit or quarry locations, producers’ names, gradings, and statement of compliance with <<ASTM C33/C33M>>  for aggregates; types, brand names, producers’ names, technical data sheets and CoCs for admixtures; and source of supply for water and ice, and properties required by <<ASTM C1602/C1602M>> for mixing water.

Except for admixtures, test results demonstrating conformance to applicable specifications shall not be older than 90 days. Test results for aggregate soundness, abrasion, and reactivity may be older than 90 days, but not older than 1 year, provided test results for the other properties specified in <<ASTM C33/C33M>> indicate that aggregate quality has not changed.

CoC confirming the source of the concrete materials (except for admixtures), that test results confirm conformance to applicable specifications, and confirming that ALL concrete materials used to develop mixture proportions correspond to those to be used in the proposed Work.1 month before placement.

          - ****Source: ACI 301 Sections 4.1.2.4, 4.1.2.5, and ACI 318-19 26.4.3.1(b)****

Field-test or trial-mixture records; and data on material and mixture proportions. Strength test records shall be less than two (2) years old. 15 work days before placement

          - ****Source: ACI 301 Sections 4.1.2.6, 4.2.2.6(b)****

Documentation verifying compliance with the specified requirements for sulfate resistance.15 work days before the initial placement.

          - ****Source: 4.1.2.6, 4.2.2.6(b)****

Documentation verifying compliance with specified requirements for freezing and thawing exposure. 15 work days before the  initial placement.

          - ****Source: ACI 301 Sections 4.1.2.6, 4.2.2.6(d)****

Documentation verifying compliance with specified requirements for low permeability. 15 work days before the  initial placement.

          - ****Source: ACI 301 Sections 4.1.2.6, 4.2.2.6(e)****

Documentation verifying compliance with specified requirements for corrosion resistance. 15 work days before the initial placement.

          - ****Source: ACI 301 Sections 4.1.2.7, 4.2.2.6(a)****

Documentation verifying compliance with specified requirements for alkali-silica reaction resistance. 15 work days before the initial placement.

          - ****Source: ACI 301 Sections 4.3.2, and ASTM C94-23, 14.1****

Provide a delivery ticket for each batch of concrete at the end of each day of placement. Ensure the ticket is legible. Comply with ASTM C94/C94M Section 14.1, and the following:

Provide the following additional information:

Water-cementitious material ratio (w/cm).

Maximum amount of water permitted at the jobsite without exceeding the specified w/cm.

Water added at the jobsite

Add water at the jobsite only in the presence of a LANL technical representative, such as a field engineer or inspector.

        - ******************************************************************************

        - Review the submittals listed in this subparagraph. Omit items that are not required. Document the rationale for each deletion.

        - ******************************************************************************

Handling, placing, and constructing

          - ****Source: ACI 301 Section 5.1.2.1(a)****

Documentation of resolution of nonconformance identified on quality assurance test and inspection reports. Within 1 month after placement.

          - ****Source: ACI 301 Section 5.1.2.1(b)****

Proposed method of measuring concrete temperature. 15 work days before the  initial placement.

          - ****Source: ACI 301 Sections 5.1.2.1(c), 5.3.4.1, and PART 3 Article CONCRETE FINISHING****

Qualifications of finishing Sub-tier/Subcontractor and flatwork finishers for finishing unformed surfaces. 15 work days before the  initial placement.

          - ****Source: ACI 301 Section 5.1.2.1(d)****

Notification of concrete placement. 48 hours before initial placement, and at least 24 hours before subsequent placements.

          - ________________________

          - NOTE:  As soon as, if not prior to, “notification” is given/submitted, ensure the associated tests and inspections are coordinated properly/adequately.

          - ****Source: ACI 301 Section 5.1.2.1(e)****

List of preplacement activities. 48 hours before placement.

          - ****Source: ACI 301 Section 5.1.2.1(f)****

Agenda for preplacement meeting. 72 hours before placement.

          - ****Source: ACI 301 Section 5.1.2.1(g)****

Request to leave temporary formwork spreaders in place. 48 hours before placement.

          - ****Source: ACI 301 Section 5.1.2.1(h), 5.3.8 ACI 318-19 26.7.1.(l)****

Certifications and qualifications of Adhesive Anchor Installers. 5 days before installation.

          - ****Source: ACI 301 Section 5.1.2.2(a)****

Description of conveying equipment. 15 work days before the initial placement.

          - ****Source: ACI 301 Section 5.1.2.2(b), 5.3.7.6****

Proposed method for removal of stains, rust, efflorescence, and surface deposits. 15 work days before performing the work.

          - ****Submittals 5.1.2.2(c) -- 5.1.2.2(e) can be omitted if concreting will not occur “exposed to the elements.” Otherwise these submittals are “conservatively included” here (vs. being in Table B1) given their respective timing and since predicting the weather is difficult. If concreting will occur exposed to the elements, but it’s somehow known with certainty that one or more of these submittals is not necessary, the submittal(s) can be omitted. ****

          - ****Source: ACI 301 Section 5.1.2.2(c), 5.3.2.1(a) and PART 3 Article CURING AND PROTECTION****

Proposed wet-weather protection activities. Project EOR and/or LANL STR can waive this submittal if concreting will not be (or was not) performed during “wet weather.” 48 hours before placement.

          - ****Source: ACI 301 Sections 5.1.2.2(d), 5.3.2.1(c) and 3.8.A.3 herein****

Hot-weather Implementation Plan. Project EOR and/ or LANL STR can waive this submittal if concreting will not be (or was not) performed during “hot weather.” 5 work days before placement.

          - ****Source: ACI 301 Section 5.1.2.2(e), 5.3.2.1(b)****

Cold-Weather Implementation Plan. Project EOR and/ or LANL STR can waive this submittal if concreting will not be (or was not) performed during “cold weather.” 5 work days before placement.

          - ****Source: ACI 301 Section 5.1.2.2(f)****

Methods to be used for initial curing. 5 work days before placement.

          - ****Retain 5.1.2.2(g) only if samples of exposed-aggregate finish is specified and/or indicated (elsewhere). Source: ACI 301 Section 5.1.2.2(g)****

Manufacturer’s data on retarder and proposed method of use if surface retarder is proposed for specified exposed-aggregate surface. 5 work days before beginning finishing.

          - **** A bonded two-course slab consists of a base slab plus a bonded topping, and is typically used only in applications involving heavy-duty industrial vehicular traffic. Refer to ACI 302.1R for more detail. Source: ACI 301 Sections 5.1.2.3(a), 5.3.4.2(f) ****

If bonding material other than cement grout is proposed for two-course slabs or construction joints, submit applicable specification and manufacturer’s data on bonding agent. 5 work days before beginning finishing.

          - ****Retain 5.1.2.2(i) only if underwater placement will be necessary/potentially necessary. Source: ACI 301 Section 5.1.2.2(i)****

Proposed method for underwater placement. 5 work days before placement.

          - ****Retain 5.3.3.2 only if a sample finish is furnished to the subcontractor to reproduce. Source: 5.3.3.2****

Sample finish (for finishing formed surfaces when/if matching sample finish is required). 5 work days before beginning finishing.

      - ***************************************************************************************

      - Retain the following paragraph if required by the project. Verify the requirements below against LANL ESM Chapter 14 - Sustainable Design, Attachment 1 "Required Attribute" Column and, if applicable, the LEED prerequisites and project credits. Material content is required.

      - ***************************************************************************************

Sustainable Design (SD) Submittals: Provide material content documentation in accordance with the requirements of this Section.​​​<< Submit any additional documentation for this product category, as applicable under Section  01 8113.13 - Sustainable Design with this Section's submittal.; or  None - N/A>>​​​

DESIGN CHANGES

If an item listed in Appendix A Design Change(s) applies, it shall be resolved using a Field Change Request (FCR) or other LANL-Engineering-approved method.

QUALITY ASSURANCE

Comply with the following documents unless this Section specifies otherwise: the version of <<ACI SPEC-301>> referenced by the applicable edition of <<ACI CODE-318>>, Section << 01 4000 - Quality Requirements - Non-Nuclear>>, and latest <<CRSI (P1)>>. Notify the LANL STR if a conflict occurs between this Section and these documents.

Permit inspection of the Work at all times by LANL and the LANL Independent Testing Agency to verify compliance with this Section. Interim inspections do not constitute acceptance of defective work or materials.

Use cement, aggregate, and pozzolan or supplementary cementitious material (SCM) from the same sources used to develop the approved mixture proportions.

Provide a Certificate of Conformance (CoC) that identifies material sources, confirms compliance with applicable specifications.

Use separate concrete mixtures for different portions of the Work only when each mixture complies with its specified requirements. Provide a CoC for each mixture.

      - ***************************************************************************************

      - ACI 318 (Sections 26.5.4.1(a) and 26.5.5.1(a)) require the EOR to indicate in the construction documents the temperature limits for concrete as delivered in cold and hot weather, respectively.  Ensure these limits (i.e., max. and min. temperatures) are indicated herein and/or on the Drawings.

      - - For guidance on establishing the cold-weather limits, see ACI 301 Section 4.2.2.5; ACI 306R, Table 5.1; and ASTM C94 Section 12.11.

      - - For guidance on establishing the hot-weather limits, see ACI 301 Section 4.2.2.5; ACI 305R Section 4.4; ASTM C94 Section 12.12; and ACI 305.1 Section 3.2.1.

      - PART 3 Article Curing and Protection stipulates that these limits shall be met.

      - ***************************************************************************************

Perform curing, hot-weather concreting, and cold-weather concreting in accordance with <<ACI SPEC-301>> and the approved Hot-Weather and Cold-Weather Implementation Plans.

See PART 3 Article CURING AND PROTECTION for details of these plans and their development.

Testing Agency Qualifications: Use testing agencies that meet the following requirements:

Concrete testing agencies: accredited in accordance with <<ASTM C1077>>.

Reinforcing steel testing agencies: comply with <<ASTM E329>>.

Obtain approval of testing agencies and personnel from the LANL Building Official or designee in accordance with the <<ICC (IBC)>> and LANL ESM Chapter 16 - Building Code Program.

      - ***************************************************************************************

      - Retain the following two paragraphs for reinforced concrete.

      - ***************************************************************************************

Maintain heat number traceability for reinforcement. Ensure heat or lot numbers on bundle tags correspond to the associated CMTRs. Verify tags during receiving inspection. After verification, retain tags and submit them with documentation.

Do not use foreign reinforcement unless LANL authorizes its use.

Welder Qualifications:  Welding processes and welding operators qualified in accordance with <<AWS D1.4/D1.4M>> and no more than ​<< 12 months; or  ____>>​ before start of scheduled welding work.

Perform welding of reinforcing bars only after approval by the Engineer of Record and LANL.

Use welding procedures approved by the Engineer of Record and LANL.

        - ******************************************************************************

        - Choose the applicable option(s) in the following subparagraph. Include Section << 01 4455 - Onsite Welding, Brazing and Joining Requirements>> - if field welding is permitted.

        - ******************************************************************************

Comply with  <<ACI SPEC-301>> Section 3.2.2.2 and<<AWS D1.4/D1.4M>><< , and Section 01 4455 - Onsite Welding, Brazing and Joining Requirements; and  None - N/A>>.

Do not use reinforcing bars as filler metal, gap filler, or for other welded applications.

Provide CMTRs that demonstrate compliance with <<AWS D1.4/D1.4M>> for reinforcing bars other than <<ASTM A706/A706M>>.

Use a batch plant that holds current certification under the NRMCA certification program.

Calibrate devices used for acceptance or testing in accordance with recognized tolerances and national standards, including NIST.

Mark each device for traceability to calibration records and indicate recalibration due dates.

Maintain a usage log. Report devices found out of tolerance to the LANL STR within 3 working days. Include identification of affected work and device usage.

Report devices found out of tolerance to the LANL STR within 3 working days. Include identification of affected work and device usage.

DELIVERY, STORAGE AND HANDLING

Store cementitious materials and aggregates to prevent deterioration and contamination.

Do not use material that has deteriorated or become contaminated.

      - ***************************************************************************************

      - Request approved formwork calculations when required.

      - ***************************************************************************************

Do not deliver concrete until vapor retarder or barrier, formwork, reinforcement, embedded items, chamfer strips, and prerequisites identified in the project “Test and Inspection Plan” are in place and ready for placement.

Store materials at the jobsite in accordance with <<ACI SPEC-301>>. Maintain identification of materials after bundles are broken and tags are removed.

Perform inspection and documentation verification at delivery to the site receiving area before off-loading and incorporation into the Work.

Verify compliance with specified requirements and project environmental, safety, health (ES&H), and radiological requirements.

Review materials, shipping documentation, safety data sheets, data sheets, test reports, and shipping manifests.

Mark nonconforming materials and prevent entry to the site or place them in an off-site quarantine area until verification is complete.

        - ******************************************************************************

        - Retain the following 4 subparagraph if applicable.

        - ******************************************************************************

Store reinforcement by size and shape in separate piles on racks above the ground to limit corrosion.

Protect reinforcement from grease, oil, and dirt.

Maintain identification of bar sizes after bundles are broken and tags are removed.

Obtain written approval from the Engineer of Record before painting reinforcement.

PART 2 - PRODUCTS

GENERAL REQUIREMENTS

All concrete Work, products, and materials shall conform to applicable provisions of <<ACI SPEC-301>> except as otherwise specified herein.

      - ***************************************************************************************

      - Retain one or both of the following paragraphs if required by the project.

      - ***************************************************************************************

Use guidance in <<ACI PRC-201.2>> when selecting materials for concrete mix. Apply the more stringent requirement when this Section and<<ACI PRC-201.2>> differ.

Refer to LANL ESM Chapter 14 - Sustainable Design, Attachment 1 for Environmentally Preferable Products for Concrete.

      - ***************************************************************************************

      - Retain the following Article, along with applicable paragraphs and subparagraphs, as required by the project.

      - ***************************************************************************************

FORM MATERIALS AND ACCESSORIES

Smooth-Formed Finished Concrete: Use form-facing panels that provide continuous, true, and smooth concrete surfaces. Furnish in the largest practicable sizes to minimize joints. Acceptable materials include:

Plywood, metal, or other approved panel materials, as follows:

Use metal form surfaces free of irregularities, dents, or sags.

Use exterior-grade plywood panels, suitable for concrete forms, complying with <<APA PS 1>>, and as follows:

High-density overlay, Class 1 or better.

Medium density overlay, Class 1 or better; mill-release agent treated and edge-sealed.

Structural 1, B-B or better; mill-oiled and edge-sealed.

B-B (Concrete Form), Class 1 or better; mill-oiled and edge-sealed.

<<CPA A135.4>>, hardboard for smooth form lining.

Prefabricated forms.

Preformed Steel Forms: Minimum 16 gage matched, tight fitting, stiffened to support weight of concrete without deflection detrimental to tolerances and appearance of finished concrete surfaces.

Glass Fiber Fabric Reinforced Plastic Forms: Matched, tight fitting, and stiffened to avoid deflection detrimental to tolerances or finished appearance.

Pan Type: Glass fiber, sized and profiled as required.

Tubular Column Type: Round, spirally wound laminated fiber, surface-treated with release agent, non-reusable, sized as required.

Void Forms: Moisture-resistant treated paper faces, biodegradable, and structurally sufficient to support wet concrete until initial set; 2 in. thick.

Rough-Formed Finished Concrete: Plywood, lumber, metal, or other approved material. Provide lumber dressed on at least two edges and one side for tight fit.

Form Ties: Factory-fabricated, removable, or snap-off metal or glass-fiber-reinforced plastic form ties designed to resist lateral pressure of fresh concrete on forms and to prevent spalling of concrete on removal.

        - ******************************************************************************

        - Revise three subparagraphs below to suit Project; omit if not required.

        - ******************************************************************************

Furnish units that will leave no corrodible metal closer than 1 inch to the plane of exposed concrete surface.

Furnish ties that, when removed, will leave holes no larger than 1 inch in diameter in concrete surface.

Furnish ties with integral water-barrier plates to walls indicated to receive dampproofing or waterproofing.

Form-Release Agent: Commercially formulated form-release agent that does not bond with, stain, or adversely affect concrete surfaces and does not impair subsequent treatments of concrete surfaces.

Formulate form-release agent with rust inhibitor for steel form-facing materials.

Form release agent for form liners shall be acceptable to form liner manufacturer.

      - ***************************************************************************************

      - Retain the applicable subparagraphs of the following paragraph, as required by the project.

      - ***************************************************************************************

Accessories:

Form Ties: Snap-off or plastic-cone type free of defects that could result in surface holes larger than 1 inch.

Chamfer Strips: Wood chamfer strips, 3/4 inch × 3/4 inch.

        - ******************************************************************************

        - Include the following subparagraph if applicable. Dovetail anchor slots are cast-in-place channels in concrete walls or columns that allow masonry (brick, block, stone) to be securely tied to the concrete using dovetail anchors. They are widely used in masonry-to-concrete construction for strength, durability, and flexibility in anchoring systems.

        - Source: https://www.blok-lok.com/index.php/product/bl-303-sv-dovetail-seismic-anchor/

        - ******************************************************************************

Dovetail Anchor Slots: Galvanized steel, 22 gage, foam-filled, release-tape sealed; with anchors for securing to formwork.

        - ******************************************************************************

        - Include the following subparagraph if applicable. Flashing reglets are metal strips embedded into walls or masonry joints that hold counter-flashing securely in place, creating a watertight seal between roof and wall systems.

        - Source: https://cheneyflashing.com/product-category/masonry/reglets-counter-flashing/

        - ******************************************************************************

Flashing Reglets: Galvanized steel, 22-gauge, longest available lengths, with alignment splines, foam-filled, release-tape-sealed, with anchors for securing to formwork.

Fasteners and Hardware: Nails, spikes, lag bolts, through bolts, and anchorages of size and strength sufficient to maintain formwork in correct position during placement.

      - ***************************************************************************************

      - Revise the Waterstops paragraph below to suit Project; omit if not required.

      - The waterstop currently specified is flexible PVC, which is designed for use in construction and expansion joints with limited movement to resist the passage of fluids.

      - For more information on types of waterstops, the associated material types that are available, along with type of waterstop and material to use for a given application; refer to CRD-C513-74, CRD-C572-74, or the article “Understanding Waterstops” in The Construction Specifier.

      - ***************************************************************************************

Waterstops: Provide polyvinyl chloride (PVC) waterstops with the following properties:

Minimum tensile strength: ​<< 1,750 psi>>​.

Working temperature range: ​​<< –50 degrees F to +175 degrees F>>​​.

Ribbed profile with preformed corner sections.

Supplied in maximum possible lengths.

      - ***************************************************************************************

      - Retain the following Article, along with applicable paragraphs and subparagraphs, as required by the project.

      - ***************************************************************************************

REINFORCEMENT AND ACCESSORIES

      - ***************************************************************************************

      - Indicate reinforcing steel ASTM designation and grade in the first paragraph below per design requirements.  ASTM A706 reinforcing steel is intended for applications where controlled tensile properties, or chemical composition restrictions to enhance weldability, or both, are required.

      - This distinction is highlighted by the fact that IBC and ACI 318 have restrictions pertaining to use of ASTM A615 reinforcing steel to resist seismic forces and/or welding. These restrictions do not apply to ASTM A706.

      - -     For the seismic requirements, ref. ACI 318, 20.2.2.5(b).

      - -     For the welding requirements, ref. IBC 1705.3 and ACI 318, 26.6.4.

      - ACI 318 Section 26.6.1.1 requires including the following information in the construction documents (e.g., drawings) for ALL reinforcement (as applicable):

      - -     ASTM designation and grade of reinforcement, including applicable requirements for special seismic systems.

      - -     Type, size, location requirements, detailing, and embedment length of  reinforcement.

      - -     Concrete cover to reinforcement.

      - -     Location and length of lap splices.

      - -     Type and location of mechanical splices.

      - -     Type and location of end-bearing splices.

      - -     Type and location of welded splices and other required welding of       reinforcing bars.

      - -     ASTM designation for protective coatings of non-prestressed reinforcement.

      - -     Corrosion protection for exposed reinforcement to be bonded with  extensions on future Work.

      - In instances in which the above requirements apply to project, it is unacceptable to only refer to ACI 318 (e.g., Splices shall be per ACI 318).

      - ***************************************************************************************

Reinforcing Steel:  ​<< ASTM A615/A615M; or  ASTM A706/A706M>>​ grade 60 deformed bars, stirrups, and ties; and headed deformed bars conforming to <<ASTM A970>>, including Annex A1 requirements for Class HA head dimensions.

Accessory materials, such as proprietary mechanical splices (e.g., rebar couplers, Form Savers, Cadwelds, and others) must be supported by ICC ES Evaluation Service Reports (ICC-ESR) indicating full compliance with the applicable code of record for the project.

Welded Steel Wire Fabric:  <<ASTM A1064/A1064M>> ​<< Plain; or  Deformed>>​ type in flat sheets.

Chairs, Bolsters, Bar Supports, Spacers: Provide reinforcement supports in accordance with <<CRSI - RB4.1>> and <<ACI SPEC-301>> Section 3.

Size and shape supports to maintain reinforcement position during concrete placement. Provide load-bearing pads to prevent puncture of vapor retarders or barriers.

Use plastic-coated steel chairs, bolsters, bar supports, and spacers adjacent to concrete surfaces exposed to weather. Size and shape these supports to maintain required cover and position.

Use concrete "dobie" blocks only when documentation confirms their compressive strength is at least the compressive strength of the concrete in the placement.

Tie Wire:  Minimum 16 gage annealed type.

CONCRETE MATERIALS

Cement: Conform to <<ASTM C595/C595M>> or <<ASTM C150/C150M>>, Type I or Type II.

Fine and Coarse Aggregates: Conform to <<ASTM C33/C33M>>.

Water: Conform to <<ASTM C1602/C1602M>>.

Pozzolan: Conform to <<ASTM C618>>.

ADMIXTURES

Air Entraining admixtures: Conform to <<ASTM C260/C260M>>.

Chemical admixtures for Water reduction and Setting Time Modification: Conform to <<ASTM C494/C494M>>.

      - ***************************************************************************************

      - Retain the following Article, along with applicable paragraphs and subparagraphs, as required by the project.

      - ***************************************************************************************

MISCELLANEOUS MATERIALS

Bonding Agent: Latex bonding agent conforming to  <<ASTM C1059/C1059M>>.

      - ***************************************************************************************

      - The requirement to use a vapor retarder/barrier is derived from IBC 1907.1, which includes exceptions.  If an exception(s) applies, use of a vapor barrier is not required. See IBC Chapter 2 for vapor retarder/barrier definition, and ACI 360R-24, Figure 4.7 for additional guidance.

      - ***************************************************************************************

Vapor Retarder/Barrier: Provide polyethylene sheeting conforming to <<ASTM E1745>> Class << C; or  ______>>, with a minimum thickness of << 6; or  _______>> mil and a maximum permeance rating of << 0.04; or  _______>> perms, determined per <<ASTM E96>>.

Grout and Concrete Repair Materials: Refer to Section << 03 6000 - Grouting>>.

Isolation/Expansion Joint Filler: Provide asphalt-impregnated fiberboard or felt conforming to <<ASTM D1751>>.

Curing Compound: Conform to <<ASTM C309>> or <<ASTM C1315>>.

Curing Sheet Materials: Conform to <<ASTM C171>>.

CONCRETE MIX DESIGN

General Requirements

Proportion concrete to achieve the required average compressive strength, f′cr, as determined per <<ACI SPEC-301>>.

Produce concrete to minimize the frequency of strength test results falling below the specified compressive strength, f′c.

The concrete strength, f’c, shall be based on 28-day tests in accordance with <<ASTM C39/C39M>>.

Account for effects on workability, setting time, strength development, curing, and other performance characteristics of concrete mixes that contain pozzolan, fly ash, or other supplementary cementitious materials. Adjust construction activities to reflect these effects, including form removal and shoring times.

Use accelerating admixtures in cold weather only after approval as part of the design mix before use. Do not relax cold-weather placement requirements when using admixtures.

Do not use calcium chloride as an admixture.

Use set-retarding admixtures in hot weather only after approval as part of the design mix before use.

Selection of Concrete Proportions

Evaluate each combination of materials separately when different concrete mixes are used for different portions of the work.

Establish concrete proportions to provide:

Workability and consistency suitable for placement conditions, allowing proper consolidation around reinforcement without segregation or excessive bleeding.

Resistance to special exposures as required below by the "Durability Requirements" paragraph.

Compliance with strength requirements provided ​<< below under "Normal Weight Concrete Requirements";  on the construction Drawings; or  ______>>​.

Determine concrete mixture proportions in accordance with Article 4.2.3 of <<ACI SPEC-301>>.

      - ***************************************************************************************

      - To ensure that the following “Durability-Requirements Paragraph” is complied with, the EOR shall assign the exposure categories and classes (ref. ACI 318 Ch. 19) on the construction Drawings and/or under the Normal Weight Concrete Requirements paragraph below.

      - ***************************************************************************************

Durability Requirements

Comply with the applicable provisions indicated ​​​<< below under "Normal Weight Concrete Requirements";  on the construction Drawings; or  ______>>​​​.

      - ***************************************************************************************

      - ASR is the reaction between the alkali hydroxide in Portland cement and certain siliceous rocks and minerals present in the aggregates, such as opal, chert, chalcedony, trydymite, cristobalite, strained quartz, etc. The products of this reaction often result in significant expansion and cracking of the concrete, and ultimately failure of the concrete structure, including significant potential for foreign object damage. For additional details refer to PCA Alkali-Aggregate Reaction and Federal Highway Administration Alkali-Silica Reactivity Program.

      - Include the limits on soluble alkalies for Portland cement and for pozzolan whenever there is a possibility of alkali-aggregate reactive aggregates being furnished, refer to ASTM C1778 for details. In addition, note that EPA Comprehensive Procurement Guidelines (CPG) program recommends that procuring agencies use concrete and other cementitious materials containing coal fly ash (pozzolan).

      - ***************************************************************************************

Standard Mix Design: Use a maximum of 25 percent, by weight of total cementitious material, Class N pozzolan or Class F fly ash conforming to <<ASTM C618>> to mitigate alkali-silica reaction (ASR) associated with siliceous aggregates in Northern New Mexico.

      - ***************************************************************************************

      - Retain the following paragraph if required by the project.

      - ***************************************************************************************

Alternative Mix Designs: Alternate methods for mitigating ASR, including use of ground slag, Type F fly ash, Class N pozzolan, silica fume, or lithium compound admixtures, are acceptable when supported by tests and documentation submitted to LANL and approved per PART 1, Article SUBMITTALS.

Provide mix designs without the cementitious material required for the standard mix design only when aggregate testing demonstrates reactivity less than 0.1 percent. Test aggregates in accordance with <<ASTM C1260>>​ or an approved alternate method.

Demonstrate ASR resistance for concrete that contains pozzolan, slag cement, or fly ash in accordance with <<ASTM C1567>>.

Proportion concrete in accordance with <<ACI SPEC-301>> Section 4.

Obtain a formal variance to this Section for mix designs that exceed the limits defined in the paragraph on Normal Weight Concrete Requirements, including slump, air content, and water-cementitious materials ratio.

Normal Weight Concrete Requirements: Provide Ready-Mixed concrete meeting the requirements of <<ASTM C94/C94M>>​, and the requirements of this Section, including the following:

        - ******************************************************************************

        - For each concrete mixture, the EOR is required (by ACI 318, Section 26.4.2.1) to specify the following items based on (EOR-) assigned exposure classes* or (EOR’s) design of members in the drawings:

        - 1.     Minimum specified compressive strength of concrete, f’c.

        - 2.     Test age for demonstrating compliance with f’c if different from 28 days.

        - 3.     Maximum w/cm applicable to most restrictive assigned durability exposure class.

        - 4.     Nominal maximum size of coarse aggregate not to exceed the least of (i), (ii), and (iii):

          - i.     one-fifth the narrowest dimension between sides of forms

          - ii.     one-third the depth of slabs

          - iii.     three-fourths the minimum specified clear spacing between individual reinforcing bars or wires, or bundles of bars

          - For the default value for aggregate size (i.e., 0.75”), the above ‘translates’ to the following limiting (and ‘code-compliant’) scenario (based on i–iii):  members and slabs as thin as 4” and 2.5”, respectively; and rebar/rebar bundles spaced as close as 1”.

        - 5.     For members assigned to Exposure Classes F1–F3, air content from ACI 318 Section 19.3.3.1.

        - 6.     For members assigned to Exposure Category C, applicable chloride ion (CL-) limits for assigned Exposure Class (i.e., C0–C2) from ACI 318 Section 19.3.2.1.

        - 7.     For members assigned to Exposure Classes S1–S3, type of cementitious materials from ACI 318 Section 19.3.2.1.

        - 8.     Target slump meeting the requirements in this section and the subcontract documents. Target slump must not exceed 9 in. Concrete must not show visible signs of segregation.

        - * ACI 318 Ch. 19 requires the EOR to “…assign exposure classes in accordance with the severity of the anticipated exposure of members for each exposure category in Table 19.3.1.1. The typical exposure category (in Table 19.3.1.1) of concern at LANL is F, Freezing and Thawing, and the typical upper-bound severity of exposure is Severe (i.e., F2).

        - Given the above, the default values for min. f’c, nominal maximum aggregate size, maximum water/cementitious materials ratio, and air content that appear in the “Exterior concrete” subparagraphs below corresponding to 4500 psi are based on achieving “F2 class concrete”. Added benefits of F2 class concrete are that such concrete also meets the ‘low-permeability requirements (i.e., W1),’ and the ‘no-concern-for-sulfate requirements (i.e., S0),’ of ACI 318 Chapter 19.

        - For projects that involve F3 exposure class; or Sulfate (S1–S3) and/or Corrosion (C0–C2**) exposure categories, use of solely the criteria for ‘exterior’ concrete (i.e., listed in the first three subparagraphs below), whether or not the default values (described above) are used, will NOT ensure that the resulting concrete meets the durability requirements of ACI 318 Ch. 19.

        - **Note that C0 class does not mean that “corrosion can be ignored.” As is indicated in ACI 318 Table 19.3.2.1, the ingredients of “C0 (and C1) concrete” must be tested for the quantity of CL-.

        - If the design or construction requirements dictate that in-place strength of concrete must be achieved at specific ages or stages of construction, the EOR must indicate such.

        - If f’c > 5,000 psi, per ACI 318 Section 26.4.4.1(b), test data documenting the characteristics of the proposed mix are required.

        - To increase the likelihood of good quality control, limit the number of concrete mixtures used on a project to as few as necessary. The required average compressive strength (f’cr) for the batch plants that supply concrete to LANL can be calculated per ACI 301 Table 4.2.3.1 or based on available field strength test records.

        - Retain the applicable subparagraphs from the following five.

        - ******************************************************************************

Exterior concrete exposed to freezing and thawing

Minimum compressive strength, f’c : ​​<< 4,500 psi @ 28 days; or  _______>>​​.

Maximum nominal aggregate size: ​​<< 0.75 in.; or  _______>>​​

Maximum water/cement ratio: ​​​<< 0.45; or  _______>>​​​

Slump: ​​<< 4 inch; or  _______>>​​

Air content: ​​<< 6; or  _______>>​​ percent.

Exposure categories and classes:

Freezing and Thawing, Class: ​<< F0;  F1;  F2; or  F3>>​

Sulfate, Class: ​<< S0;  S1;  S2; or  S3>>​

In contact with water, Class: ​<< W0;  W1; or  W2>>​

Corrosion protection of reinforcement Class: ​<< C0;  C1; or  C2>>​

Exterior concrete (pumpable), exposed to freezing and thawing(1)

Minimum compressive strength, f’c : ​​<< 4,500 psi @ 28 days; or  _______>>​​.

Maximum nominal aggregate size: ​​<< 0.75 in.; or  _______>>​​

Maximum water-cementitious materials ratio: << 0.45; or  _______>>.

Slump: ​​<< 6 inch; or  _______>>​​ at discharge of truck.

Slump: ​​<< 3 to 7 ½ inch; or  _______>>​​ at pump discharge.

Air content: << 6; or  _______>> percent.

Exposure categories and classes:

Freezing and Thawing, Class: ​​<< F0;  F1;  F2; or  F3>>​​

Sulfate, Class: ​​<< S0;  S1;  S2; or  S3>>​​

In contact with water, Class: ​​<< W0;  W1; or  W2>>​​

Corrosion protection of reinforcement Class: ​​<< C0;  C1; or  C2>>​​

        - NOTE (1): PART 3 Article FIELD QUALITY CONTROL, requires slump, strength, temperature, and air-content criteria be met at pump discharge—that is, samples for testing are taken at the placement-end of the pipe/hose. This requirement does not change/alter the <<ACI SPEC-301>> or <<ASTM C94/C94M>> tolerances for the criteria (i.e., the tolerances apply to test results on samples taken at the placement-end of pipe/hose).

        - ******************************************************************************

        - Caution - 5000 psi concrete is prone to hairline cracking.

        - ******************************************************************************

Exterior concrete exposed to freezing and thawing

Compressive strength, f’c: ​​<< 5000 psi @ 28 days; or  _______>>​​.

Maximum nominal aggregate size: ​​<< 0.75 inch; or  _______>>​​.

Maximum water-cementitious materials ratio: << 0.40; or  _______>>.

Slump: ​​​<< 4 inch; or  _______>>​​​.

Air Content: << 6; or  _______>> percent.

Exposure categories and classes:

Freezing and Thawing, Class: ​​​<< F0;  F1;  F2; or  F3>>​​​

Sulfate, Class: ​​​<< S0;  S1;  S2; or  S3>>​​​

In contact with water, Class: ​​​<< W0;  W1; or  W2>>​​​

Corrosion protection of reinforcement Class: ​​​<< C0;  C1; or  C2>>​​​

Interior concrete not exposed to freezing and thawing

Compressive strength, f’c: ​​<< 3,000 psi @ 28 days; or  _______>>​​.

Maximum nominal aggregate size: ​​<< 0.75 inch; or  _______>>​​.

Maximum water-cementitious materials ratio: << 0.55; or  _______>>.

Slump: ​​<< 4 inch; or  _______>>​​.

Air content: << 3; or  _______>> percent maximum.

Exposure categories and classes:

Freezing and Thawing, Class: ​​​<< F0;  F1;  F2; or  F3>>​​​

Sulfate, Class: ​​​<< S0;  S1;  S2; or  S3>>​​​

In contact with water, Class: ​​​<< W0;  W1; or  W2>>​​​

Corrosion protection of reinforcement Class: ​​​<< C0;  C1; or  C2>>​​​

Interior concrete not exposed to freezing and thawing

Compressive strength, f’c: ​​<< 4,000 psi @ 28 days; or  _______>>​​.

Maximum nominal aggregate size: ​​<< 0.75 in.; or  _______>>​​

Maximum water-cementitious materials ratio: << 0.45; or  _______>>.

Slump: ​​<< 4 inch; or  _______>>​​

Air content: << 3; or  _______>> percent maximum.

Exposure categories and classes:

Freezing and Thawing, Class: ​​​<< F0;  F1;  F2; or  F3>>​​​

Sulfate, Class: ​​​<< S0;  S1;  S2; or  S3>>​​​

In contact with water, Class: ​​​<< W0;  W1; or  W2>>​​​

Corrosion protection of reinforcement Class: ​​​<< C0;  C1; or  C2>>​​​

      - ***************************************************************************************

      - The pre-approved concrete mix designs included in the Listing of LBO-Approved IBC Testing, NDE and Inspection Agencies; Fabricators; and Products associated with LANL ESM Chapter 16 - Building Code Program are permitted for use for concrete of the following exposure classes:

      - Exterior mixes (4500 psi): F0 – F2, S0, W0 – W1, and C0 – C1

      - Exterior mixes (5000 psi): F0 – F3, S0, W0 – W1, and C0 – C1

      - Interior mixes (4000 psi): F0 – F1, S0, W0 – W1, and C0 – C1

      - Cold weather mixes may contain accelerator admixtures, hot weather mixes may contain retarders and have increased rotation time.

      - EOR must specify minimum compressive strength of concrete, f’c on the drawings (e.g., in the General Notes of applicable drawings), and whether the design mix is interior or exterior.

      - Note: Exterior mixes typically have a cementitious content that exceeds 660 lbs/ft3 (used in ACI 301-10 to define mass concrete, not in current edition). However, based on field experience with previous mix designs, the concrete resulting from such mixes behaves as “mass concrete”, typically for placement thicknesses greater than 2 ft. This can be confirmed based on their equivalent cement content (ECC) and ACI PRC-207.1-21 Figure 3.1.1.

      - For example, the equivalent cement content of some of LANL pre-approved mixes per ACI PRC-207.1-21 Equation 3.1.1 is provided below (assuming that Class N pozzolan and Class F fly ash has the same ECC, per DSO-2017-04). The EOR is responsible for performing ECC calculations for the specific mix designs used.

      - 𝐶𝐶 = 𝐶𝑒𝑚𝑒𝑛𝑡 + 0.5𝐹𝐴𝑠ℎ~𝐶𝑒𝑚𝑒𝑛𝑡 + 0.5𝑁𝑃𝑜𝑧𝑧𝑜𝑙𝑎𝑛

      - 𝐸𝐶𝐶5𝐾 = 551 + 0.5(164) = 633 𝑙𝑏/𝑦𝑑3

      - 𝐸𝐶𝐶4.5𝐾 = 524 + 0.5(156) = 602 𝑙𝑏/𝑦𝑑3

      - 𝐸𝐶𝐶4𝐾 = 477 + 0.5(143) = 549 𝑙𝑏/𝑦𝑑3

      - Given the above calculated ECC and ACI PRC-207.1-21, Figure 3.1.1 guidelines, projects using 4.5K (4500 psi) and 5K (5000 psi) (ECC > 600 lb/yd3) mixes evaluated above are required to consider the resulting concrete as potentially being “mass concrete” when the placement thickness is greater than 2 feet. Similarly, projects using 4K (4000 psi) mixes (ECC > 549 lb/yd3) evaluated above are required to consider the resulting concrete as potentially being “mass concrete” when the placement thickness is greater than 2.5 feet.

      - If any of the above conditions apply, the Project’s EOR is responsible for ensuring compliance with LANL ESM Chapter 5 - Structural, Section II.4.2, 1904.3 Mass Concrete.

      - ***************************************************************************************

LANL pre-approved concrete mix designs are included in the Listing of LBO-Approved IBC Testing, NDE and Inspection Agencies; Fabricators; and Products associated with LANL ESM Chapter 16 - Building Code Program.

Subcontractor and EOR are responsible for selecting the appropriate concrete mix design.

Subcontractor is responsible for providing Ready-Mixed concrete meeting the requirements of <<ASTM C94/C94M>>.

Blistering may occur for mixes with air content higher than 3 percent if steel trowel finishing is specified.

Admixture quantity range allows for varying dosage based on temperature.

        - ******************************************************************************

        - Retain the following subparagraph if applicable.

        - ******************************************************************************

When a pre-approved mix design is used in an ML-1 or ML-2 application, the aggregate correction factor (ACF) must be determined by testing per <<ASTM C231/C231M>>. Submit aggregate correction factor test results.

Subcontractor is responsible for verifying if the selected mixes are ‘pumpable’.

Concrete batching tolerances (e.g., cement, aggregates, water, admixtures) shall meet the requirements of <<ASTM C94/C94M>>.

PART 3 - EXECUTION

GENERAL

Perform work in accordance with <<ACI SPEC-301>> unless otherwise specified herein.

      - ***************************************************************************************

      - Edit the following if more restrictive tolerances are required by project, or if ACI 117 doesn’t address tolerances applicable to project.

      - ***************************************************************************************

Meet construction tolerances shown on the construction drawings and those in <<ACI SPEC-117>>​, or as specified in this Section, whichever is more stringent.

Ensure all inspections of formwork and reinforcing are completed prior to concrete placement.

Provide secured space, electrical power, and access for initial curing of concrete-strength-test cylinders required below by PART 3 Article FIELD QUALITY CONTROL.

      - ***************************************************************************************

      - Retain the paragraphs of the following Article that apply to the Project.

      - ***************************************************************************************

EXAMINATION

Verify lines, levels, and dimensions before proceeding with work of this section.

      - Confirm completion of required preliminary activities, including geotechnical work and soil compaction and moisture testing.

Inspect formwork, shoring, and bracing. Confirm compliance with the formwork design. Verify that supports, fastenings, wedges, ties, and related items are secure.

Verify that concrete cover for reinforcement conforms to the drawings and to the cover-related provisions in PART 3 Article INSTALLATION OF REINFORCEMENT AND OTHER EMBEDDED ITEMS, below.

Prior to placement of concrete, ensure that the Project Geotechnical Investigation report has been read and understood, soil inspections have been performed with satisfactory results, and soil testing documentation has been completed and the results are satisfactory.*

      - ________________________

      - * Refer to Sheet S-0001 of the Project structural drawings, the Statement of Special Inspections (SSI), and the Test & Inspection Plan (TIP) to determine which of these items are applicable to a given project.

      - ***************************************************************************************

      - Retain the following Article, along with applicable paragraphs and subparagraphs, as required by the project.

      - ***************************************************************************************

FORMWORK installation and removal

General

Erect formwork, shoring, and bracing to meet applicable tolerances specified in <<ACI SPEC-301>>​, <<ACI PRC-347>>, this Section and the construction Drawings. Where requirements conflict, comply with the more stringent requirements.

        - ******************************************************************************

        - Retain the following subparagraph if applicable.

        - This requirement is about preparing soil surfaces that will act as the “formwork” for concrete, and making sure they don’t compromise the quality or performance of the concrete.

        - ******************************************************************************

Hand trim sides and bottom of earth forms. Remove ice, debris, loose soil, etc. prior to placing concrete.

Verify lines, levels, centers, and dimensions before erecting formwork and confirm that layout matches construction Drawings. Verify that slabs, floors, and walls are square (90 degree corners).

Provide bracing to ensure stability of formwork. Shore or strengthen formwork subject to overstressing by construction loads.

Assemble formwork to allow for safe dismantling, stripping, and removal of principal shores without damaging concrete.

Align and seal form joints to be watertight. Minimize the number of joints.

Obtain approval from the EOR for all construction joint locations not shown on the drawings and before framing openings (in structural members) which are not detailed/shown.

Provide chamfer strips at external corners of beams, joists, columns, and walls.

Inspect erected formwork, shoring, and bracing to confirm compliance with formwork design. Verify that supports, fastenings, wedges, ties, and embedded items are secure.

Do not use wood formwork more than three times for concrete surfaces exposed to view. Do not patch formwork.

Apply form release agent prior to placement of reinforcing steel, anchoring devices, and embedded items.

Do not apply form release agent where concrete surfaces receive special finishes or applied coverings that are affected by agent. Soak inside surfaces of untreated forms with clean water. Keep surfaces coated prior to placement of concrete.

Install void forms per manufacturer’s recommendations. Protect forms from moisture or crushing.

Provide formed openings where required for items to be embedded in or passing through concrete.

Position and secure sleeves, inserts, anchors, and other cast-in-place items such that they are positioned within <<ACI SPEC-117>> tolerances and are not disturbed during concrete placement.

Clean formed cavities of debris prior to placing concrete. Clean and remove foreign matter as erection proceeds.

Install accessories per manufacturer’s instructions. Ensure items are straight, level, plumb, and undisturbed during concrete placement.

        - ******************************************************************************

        - Retain the following two subparagraphs if applicable.

        - ******************************************************************************

Install waterstops continuous without displacing reinforcement.

Install waterstops at indicated joints to form a continuous diaphragm. Use the longest practical lengths. Support and protect exposed waterstops during construction. Field-fabricate joints per manufacturer’s instructions.

Provide temporary ports or openings in formwork as needed for placement, cleaning, and inspection. Locate openings at the bottom of forms to allow drainage.

Close temporary openings with tight-fitting panels flush with the form face. Fit panels neatly to avoid visible joints in exposed concrete.

During cold weather, remove ice and snow from forms. Do not use deicing salts or water. Use compressed air or equivalent means. Ensure that water and debris drain to exterior through clean-out ports.

Do not remove forms or bracing until concrete has achieved sufficient strength to support its own weight and imposed loads without excessive deflection or creep.

Do not place construction or equipment loads on reinforced concrete until cylinder break results confirm specified strength has been achieved. Exceptions require written approval from LANL and EOR.

Removal of Formwork

Remove forms in accordance with the recommendations of <<ACI PRC-347>>.

Store and avoid damage to surfaces of removed forms intended for reuse. Discard damaged forms.

Remove forms without impairing the safety or serviceability of the structure.

Ensure concrete exposed by form removal has sufficient strength to avoid damage during removal.

Loosen forms carefully. Do not wedge pry bars, hammers, or tools against finish concrete surfaces scheduled for exposure to view.

Maintain curing in accordance with the PART 3 Article CURING AND PROTECTION, after form removal.

        - ******************************************************************************

        - Retain one or both of the following two subparagraphs, as required by the project.

        - ******************************************************************************

Formwork for parts of the Work that does not support weight of concrete or superimposed loads may be removed after cumulatively curing at not less than 50 degrees F (measured with a calibrated device) for 24 hours after placing concrete.

Leave formwork for beam soffits, joists, floor slabs, and other structural elements that support concrete weight in place until the concrete attains at least 75 percent of the 28-day design compressive strength. Confirm these elements can support their weight and approved superimposed loads before removal.

As an alternative, submit a formwork removal procedure and schedule to LANL. Base the submittal on structural analysis and concrete strength data in accordance with  <<ACI SPEC-301>> Section 2.3.4.1. Implement the procedure only after LANL approval.

Remove formwork only when shores are in place to allow removal without loosening or disturbing the shores.

After formwork removal, place construction or equipment loads on reinforced concrete only after cylinder break results indicate strengths meet specified requirements. Exceptions to this requirement must be approved in writing by the EOR and LANL STR.

      - ***************************************************************************************

      - Retain the following Article, along with applicable paragraphs and subparagraphs, as required by the project.

      - ***************************************************************************************

INSTALLATION of REINFORCEMENT and Other Embedded Items

      - ***************************************************************************************

      - Unless otherwise indicated by the EOR, the tolerances associated with placement of reinforcement ‘default’ to those stipulated in ACI 117.  Per ACI 318 Section R26.6.2.1, “…The [EOR] should specify more restrictive tolerances…when necessary to minimize the accumulation of tolerances resulting in excessive reduction in effective depth [d] or cover [cc]…”  If/when “necessary,” Section 26.6.2.1 provides (more restrictive) tolerances that can be specified. The undersides of elevated slabs, beams, etc. (i.e., “formed soffits”) are cited as an example of when more restrictive tolerances have been required.

      - ***************************************************************************************

General

Comply with applicable reinforcement installation and detailing requirements of <<ACI SPEC-301>> and <<ACI CODE-318>>. Where requirements conflict, this Section governs.

        - ******************************************************************************

        - Retain the following subparagraph if applicable.

        - ******************************************************************************

Fabricate and handle epoxy-coated reinforcing in accordance with <<ASTM D3963/D3963M>>.

Install welded wire reinforcement in the longest practical lengths. Offset end laps in both directions and secure splices with tie wire.

Verify that anchors, seats, plates, reinforcement, and other embedded items are accurately located, securely positioned, and will not interfere with concrete placement.

        - ******************************************************************************

        - Retain the applicable subparagraphs from the following two.

        - ******************************************************************************

Spiral units shall be continuous bar or wire placed with even spacing and without distortion beyond the tolerances for the specified dimensions.

For longitudinal column bars forming an end-bearing splice, ensure that the bearing ends are square cut ends and held in concentric bearing contact.

Offset bars shall be bent before placement in the forms.

        - ******************************************************************************

        - Retain the following subparagraph if applicable.

        - ******************************************************************************

Do not displace or damage vapor retarder/barrier. If vapor retarder/barrier is damaged, repair it prior to concrete placement.

Bending

Bend all reinforcement cold prior to placement using industry-standard equipment and procedures unless otherwise permitted by the EOR.

Do not field-bend reinforcement partially embedded in concrete unless shown on the construction drawings or specifically permitted by the EOR.

If field bending is shown in the construction documents, comply with <<ACI SPEC-301>> requirements for field bending and straightening.

Surface Conditions of Reinforcement

        - ******************************************************************************

        - Surface rust on uncoated (“black”) reinforcing bars is common in construction environments, as ferrous materials naturally corrode. Tightly adhered rust is not detrimental to bond performance and may, in some cases, be beneficial. Minor red or brown surface rust, as illustrated in Figure 5, is acceptable. Even heavier, uniform rust buildup, such as that shown in Figure 6, does not typically impair bond behavior.

        - However, advanced corrosion resulting in flaky or laminar rust should be removed. Such removal is generally achieved through normal handling or by lightly striking the bars. Cleaning reinforcing bars in the field can be time-consuming and costly, and excessive cleaning—such as over-polishing with a wire brush or flapper wheel—may adversely affect bond performance.

        - Despite changes in reinforcing steel manufacturing processes over time, laboratory evidence indicates that moderate surface contaminants have little to no detrimental effect on bond strength.

        - Source: CRSI ETN-M-5-24 Rust, Mill Scale, and Other Surface Contaminants on Steel Reinforcing Bars

        - Retain one of the following subparagraphs.

        - ******************************************************************************

At the time of concrete placement, ensure reinforcement is free from mud, oil, or other nonmetallic coatings that reduce bond.

        - *** OR ***

Clean reinforcement of loose, flaky, or laminar rust, and other contaminants that reduce bond. Tightly adhered rust is acceptable

Placing Reinforcement

Accurately position, support, and secure reinforcement to ensure minimum concrete cover is achieved for corrosion protection.

Do not weld crossing bars for assembly unless authorized by the EOR.

        - ******************************************************************************

        - Retain one or both of the following subparagraphs if applicable.

        - ******************************************************************************

Bars may be moved to avoid interference with other reinforcement, conduits, or embedded items only with EOR approval.

If bars are moved beyond permitted tolerances, obtain EOR approval for the revised arrangement before proceeding.

Concrete Protection for Reinforcement

        - ******************************************************************************

        - The following minimum reinforcement-cover requirements are per ACI 318 Section 20.5.1 and are applicable only to cast-in-place, non-prestressed concrete members, and in instances where greater cover is not required by fire-protection requirements.

        - The following does not include the ACI 318 cover requirements for headed shear stud reinforcement, coated reinforcement, or embedments.

        - Finally, for SDC D, diaphragm collector cover might be governed by ACI 318 Section 18.12.7.7.

        - ******************************************************************************

Cast-in-place concrete (nonprestressed) –The following minimum concrete cover shall be provided for reinforcement:

        - Table 3-1 Minimum Concrete Cover

| Condition | cover, in. |
| --- | --- |
| Concrete cast against and permanently exposed to earth | 3 |
| Concrete exposed to earth or weather: |  |
| No. 6 through No. 18 bars | 2 |
| No. 5 bar, and smaller | 1-1/2 |
| Concrete not exposed to weather or in contact with ground: |  |
| Slabs, walls, joists: |  |
| No. 14 and No. 18 bars | 1-1/2 |
| No. 11 bar and smaller | 3/4 |
| Beams, columns: |  |
| Primary reinforcement, ties, stirrups, spirals6 | 1-1/2 |

Conflicts Between Table 3-1 and the Construction Drawings

If Drawing requirements exceed Table 3-1, use the Drawing requirements.

If Table 3-1 requires greater cover than shown on the Drawings:

Request LANL STR direction.

Do not place concrete until cover discrepancies are resolved.

      - ***************************************************************************************

      - Retain the following paragraph and applicable subparagraphs, as required by the project.

      - ***************************************************************************************

Conduits and Pipes Embedded in Concrete

Do not embed conduits, pipes, or sleeves in concrete without prior approval from EOR.

Only use Conduits, pipes, and sleeves made of materials not harmful to concrete and do not structurally replace displaced concrete, except as permitted under Conduits Considered as Structurally Replacing Concrete (below).

Do not embed aluminum conduits or pipes in structural concrete unless they are effectively coated or covered to prevent aluminum–concrete reactions or electrolytic action with steel.

Ensure conduits, pipes, and sleeves passing through slabs, walls, or beams do not significantly impair structural strength.

BATCHING, MIXING AND TRANSPORT

Batch all concrete using automated equipment with digital recording capabilities.

Mix concrete until a uniform distribution of materials is achieved. Fully discharge each batch before recharging the mixer.

Mix and deliver ready-mixed concrete in accordance with <<ASTM C94/C94M>>​.

Slump

Unless otherwise specified or approved by LANL, determine concrete slump at the point of placement.

Perform slump testing in accordance with <<ASTM C143/C143M>>.

Comply with slump tolerance requirements of <<ACI SPEC-117>>​.

      - ***************************************************************************************

      - The following paragraph aims to prevent excessive field water additions into the concrete mix. Nevertheless, there are other situations that may impact the w/cm ratio. For instance, for slab-on-grade (SOG) without a vapor retarder/barrier the water content of the underlying soil may affect the w/cm ratio of the placed concrete. Thus, for SOG without vapor retarder/barrier, ensure the Project Specification package includes Section ​<< 31 2000 - Earth Moving>>​ edited for compliance with the Geotechnical Report.

      - ***************************************************************************************

Adding Mixing Water in the Field

Adding mixing water in the field is permitted only if:

The ready-mix producer intentionally held back water at the batch plant; and

The slump after transport is less than the value specified in the construction documents.

Do not exceed the specified water-cementitious materials ratio.

Reduce the maximum allowable water-holdback volume by 10 percent to account for measuring technique accuracy.

Field addition of water is permitted only when one of the following measuring devices is used:

A LANL-approved calibrated mechanical device, or

The ready mix truck sight glass, provided that:

The sight glass is be manually verified prior to water addition.

Verification is performed by dispensing water into a graduated container and comparing the measured value with the device reading.

Verification confirms the sight glass accuracy within ±5 percent.

The volume of water added is adjusted based on the verification results.

PLACING CONCRETE

Notify the LANL STR a minimum of 24 hours prior to commencement of concrete operations.

Remove standing water from place of deposit before concrete is placed, unless permission to do otherwise is granted by LANL.

Place concrete in accordance with <<ACI PRC-304>>. Follow <<ACI PRC-304.2>> for pumping of concrete and <<ACI PRC-304.4>> for belt conveying.

Place concrete for floor slabs in accordance with <<ACI PRC-302.1>>.

Consolidate concrete by internal vibration per <<ACI SPEC-301>> or <<ACI PRC-309>>; whichever is more stringent, unless otherwise directed by the EOR.

      - ***************************************************************************************

      - Retain the following paragraph if applicable.

      - ***************************************************************************************

Pre-wet masonry filler units that will be in contact with concrete prior to placing concrete.

Do not transport/pump concrete using pipe or chutes made of aluminum or aluminum alloys.

Deposit concrete as close as practicable to its final position to avoid segregation due to rehandling or flowing.

Place concrete at a rate that maintains plasticity and allows it to flow readily into spaces between reinforcement.

Maintain records of concrete placement. Record date, location, quantity, air temperature, and number and type of test samples taken.

Ensure ​​​<< reinforcement;  inserts;  waterstops;  embedded parts;  formed construction joint devices; and  ______>>​​​ will not be disturbed during concrete placement.

Place concrete continuously without construction (cold) joints until the panel or section, as defined by boundaries or predetermined joints, is completed.

Where construction joints are permitted, before next placement prepare joint surface as required by the “Construction-Joints" Paragraph under  CONCRETE JOINTS.

Ensure top surfaces of vertically formed lifts are generally level.

Finish floors level and flat, unless otherwise indicated, within the tolerances specified.

Thoroughly consolidate concrete during placement using suitable means. Work concrete around reinforcement, embedded fixtures, and into corners of forms.

Do not use concrete that has been contaminated or has lost its initial workability to the extent that it can no longer be consolidated by the intended method(s).

Placement Time and Drum Revolution Counter

Do not use re-tempered concrete.

Mixture Designs with Target 1-1/2-Hour Maximum Placement Time:

Place Central-Mixed concrete within 300 revolutions and 1-1/2 hours after initial mixing.

Place shrink-mixed and truck-mixed concrete within 100–300 revolutions and 1-1/2 hours after initial mixing.

The above time and revolution limits may be exceeded only when both of the following conditions are met:

The concrete slump or slump flow allows placement without adding water.

Air content, slump, and temperature meet specified requirements and are verified through additional testing at the point of delivery.

Acceptance testing, at the required frequencies specified in the Frequency of Testing paragraph under FIELD QUALITY CONTROL, is performed at the point of placement.

Mixture Designs with Extended Placement Time:

Do not place concrete beyond the maximum design placement time.

Reject concrete that exceeds the design placement time.

When concrete is placed within the allowable design placement time, record the drum revolution counter on the batch ticket; no revolution limit applies.

Temperature Conditions

When ambient temperature is below 40 degrees F or above 80 degrees F, implement the approved cold- or hot-weather concreting plan, respectively.

Maintain records of concrete temperatures and the protection provided during placement and curing.

      - ***************************************************************************************

      - Retain the applicable paragraphs from the following four paragraphs, as required by the project.

      - ***************************************************************************************

Install vapor retarder/barrier under interior slabs-on-ground prior to concrete pour.  Lap joints minimum 6 inches and seal watertight by sealant applied between overlapping edges and ends or taping edges and ends.

      - ***************************************************************************************

      - Include the paragraph below if the slab-on-ground is part of the seismic force-resisting system. Also see related author note associated with Article Contraction Joints.

      - ***************************************************************************************

Build slabs-on-ground that are indicated as being part of the seismic force-resisting system monolithically with vertical surfaces, unless otherwise shown/detailed/called out in the design drawings.

      - ***************************************************************************************

      - Include the following paragraph it the project involves construction of concrete beams, girders, brackets, column capitals, haunches, and drop panels monolithically build with the slab

      - ***************************************************************************************

Modify <<ACI SPEC-301>>, Section 5.3.2.4(g) to read as follows:

        - 5.3.2.4(g) Place concrete for beams, girders, brackets, column capitals, haunches, and drop panels at same time as concrete for adjacent slabs, unless otherwise shown.

      - ***************************************************************************************

      - Retain the following paragraph if the project involves placement of members supported by columns or walls.

      - ***************************************************************************************

Cast Beams, girders, or slabs supported by columns only after the concrete in the vertical support members is no longer plastic.

      - ***************************************************************************************

      - Retain the following paragraph If floor system concrete strength is less than 70 percent of column concrete strength,

      - ACI 318 Section 26.5.7.1(d) requires the EOR to indicate locations where slab and column placements must be integrated during placement (per ACI 318 Section 15.5).

      - ACI 318 Section 26.5.7.1(c) requires EOR to provide details for construction of sloped or stepped footings designed to act as a unit.

      - ***************************************************************************************

At locations where slab and column placements must be integrated, extend column concrete at least 2 feet into the floor system from the column face for the full depth of the floor system. Integrate column concrete with floor concrete.

CONCRETE JOINTS

      - ***************************************************************************************

      - Per ACI 318, Section 26.5.6.1, the EOR must provide locations, surface preparation, and details of construction, isolation, and contraction joints (if such joints are required by the design).

      - The same section includes “Design information” requirements pertaining to transfer of forces through construction joints, and ‘surface preparation.’  If any of these requirements apply to the project then the respective portions of Section 26.5.6.1 must be followed and included below.

      - ***************************************************************************************

Construction Joints

Locate construction joints as shown on the construction drawings or as approved by EOR.

        - ******************************************************************************

        - Retain one or both of the following subparagraphs if applicable.

        - ******************************************************************************

In floor systems, locate construction joints within the middle third of slab, beam, and girder spans.

Offset construction joints in girders by a minimum of two times the width of intersecting beams.

        - ******************************************************************************

        - Laitance is a weak layer of cement and fine aggregate on a concrete surface that is usually caused by an over-wet mixture, overworking the mixture, improper or excessive finishing or combination thereof.

        - ******************************************************************************

Prepare hardened concrete at construction joints by removing all laitance and materials that may inhibit bond by using a steel brush, pressure washing, or other approved methods.

        - ******************************************************************************

        - The following requirement is a designer’s choice when placing fresh concrete against hardened concrete at planned construction joints shown on the drawings. Scratch finish is another alternative refer to ACI 301 Section 5.3.2.6 for additional details.

        - Always include this requirement when placing fresh concrete against existing (hardened) concrete in existing facilities.

        - This subparagraph is consistent with ACI 318 Section 26.5.6.1(c), which applies to design for shear friction per ACI 318 Section 22.9, and to contact surfaces at construction joints for structural walls.

        - ******************************************************************************

Unless otherwise specified in the design drawings, ensure the finished surface amplitude is 1/4 inch.

Dampen construction joints (do not saturate) before placing fresh concrete. Remove all standing water prior to placement.

        - ******************************************************************************

        - The following is a designer-choice.

        - ******************************************************************************

If a bonding agent is used, perform surface preparation in accordance with the manufacturer’s written instructions.

      - ***************************************************************************************

      - Retain one or both of the following paragraphs if applicable.

      - ***************************************************************************************

Slab-on-Ground Joints

        - ******************************************************************************

        - ACI 318 Section 26.5.6.1(a) requires design, details and location of all contraction or isolation joints.

        - ******************************************************************************

Locate construction, contraction and isolation joints as indicated on the construction drawings.

Anchor joint fillers and devices to prevent movement during concrete placement.

Install joint devices, joint filler, primer, and sealant per manufacturer’s instructions.

        - ******************************************************************************

        - Retain the following subparagraph if applicable.

        - Provide contraction joint spacing per ACI 360R-24 Figure 6-6 for typical concrete.

        - ******************************************************************************

Provide contraction joints in slabs-on-ground at no more than ​​<< 15; or  _______>>​​ feet on center in each direction.

        - ******************************************************************************

        - The timing of saw cutting is critical -- it must be performed before the slab shrinks as it cools, to prevent random cracking. 4 to 12 hours is typical. In hot weather the shorter time applies. Early-entry dry-cut sawing is even earlier -- 1 to 4 hours.

        - ******************************************************************************

Saw Cut Contraction Joints: Saw cut joints before concrete begins to cool, within ​​​​<< 4 to 12 hours; or  ______>>​​​​ after placing; use ​​​​<< 3/16 inch; or  ____ inch>>​​​​ thick blade and cut at least ​​​​<< 1 inch; or  ____ inch>>​​​​ deep but not less than ​​​​<< one quarter (1/4); or  ______>>​​​​ the depth of the slab.

        - ******************************************************************************

        - Retain the following subparagraph if applicable.

        - ACI 318 Section 26.5.7.1(b) requires EOR to identify if a slab-on-ground is designed as a structural diaphragm or part of the seismic-force-resisting system.  And there is a similar requirement in IBC Section 1901.5 that applies to SDC D (i.e., "The construction documents shall include a statement if slab on grade is designed as a structural diaphragm").

        - ******************************************************************************

Saw cutting of slabs-on-ground identified in the construction documents as structural diaphragms or part of the seismic-force-resisting system is not permitted.

Load Transfer at Construction and Contraction Joints: Install load transfer devices as indicated on the construction drawings.

        - ******************************************************************************

        - Retain the following subparagraph if applicable.

        - ******************************************************************************

Construction Joints: Where not otherwise indicated, use metal combination screed and key form, with removable top section for joint sealant.

        - ******************************************************************************

        - Retain the following subparagraph if applicable.

        - For projects that include a slab-on-ground as part of the seismic force-resisting system, ensure that the detailing, location, and specification of isolation joints receive special consideration to prevent their use in a manner that could compromise the seismic performance of the structure.

        - ******************************************************************************

Isolation Joints:

Separate slabs-on-ground from vertical surfaces with 1/4 inch thick joint filler, unless otherwise shown/detailed/called out in the design drawings.

Extend joint filler from bottom of slab-on-ground to within ¼ inch of finished slab surface.

Install isolation joints as shown on the construction drawings to separate the slab from building elements such as columns, walls, equipment foundations, footings, stairs, manholes, sumps, and drains.

          - **********************************************************************

          - Retain the following subparagraph if applicable.

          - **********************************************************************

For slabs-on-ground that are part of the seismic force-resisting system, ensure isolation-joint design and placement do not interfere with seismic performance.

CONCRETE FINISHING

      - ***************************************************************************************

      - F-numbers provide a method of determining the flatness and levelness of a concrete floor slab. They are calculated using the standards set forth in ASTM E1155.

      - Floor Levelness numbers (FL) relate to slope or inclination, and generally only apply to slabs that are placed on grade, since elevated concrete slabs deflect once shores are removed. Therefore, FL numbers are only specified on elevated slabs when measurements are taken before shores and forms are removed, and the slab has no camber.

      - Floor Flatness numbers (FF) are a statistical measurement of how irregular, wavy, or bumpy a concrete floor is. FF numbers can be taken for slabs on grade as well as elevated slabs. Floor Flatness is important for spaces where equipment must be set perfectly level such as warehouses that use air-pallet jacks.

      - Floor Flatness and Levelness measurement should be taken preferably within 24 hours after placement, but not later than 72 hours after the concrete installation. In the case of an elevated slab that has camber, the structural slab must be deflected to its final shape followed by a topping finish slab that gets measured for Floor Levelness.

      - Per ACI-302.1R Figure 10.9, the following FF and FL values are acceptable for slabs on ground based on the uses listed. The EOR is responsible for specifying the appropriate floor flatness and levelness based on the expected floor usage (i.e., acceptable for the application) rather than to impose a standard that is unnecessarily exacting/demanding and costly.

| USAGE | Specified overall flatness (SOFF) | Specified overall levelness (SOFL) |
| --- | --- | --- |
| Noncritical spaces, mechanical rooms, back-of-house, parking structure slabs, areas to receive thick-set tile | 20 | 15 |
| General office, light industrial, carpeted spaces | 25 | 20 |
| General warehouse floors, areas to received thin-set tile | 35 | 25 |
| Warehouses with air-pallet use, ice rinks, gymnasium floors | 45 | 35 |
| Movie and television studios | FF >50 | FL >50 |

      - Per ACI 117 Section 4.8.5.3 minimum local values for flatness (MLFF) and levelness (MLFL) shall equal 3/5 of the SOFF and SOFL values, respectively, unless noted otherwise below by the EOR. For additional tolerance guidance refer to ACI-302.1R Tables 10.15.3 a and b.

      - Note: Broom finish is commonly specified for parking lots and other exterior concrete, SOFF and SOFL greater than 20 and 15 respectively, are in general not achievable for slabs with broom and other textured finishes.

      - Retain the following paragraph if applicable.

      - ***************************************************************************************

Unless noted otherwise, finish interior slabs on ground to the following specified overall values of flatness, SOFF ​​​​<< 35; or  _______>>​​​​, and of levelness, SOFL ​​​​<< 25; or  _______>>​​​​; with minimum local value of flatness, MLFF ​​​​<< 24; or  _______>>​​​​; and of levelness, MLFL ​​​​<< 17; or  _______>>​​​​, measured in accordance with <<ASTM E1155/E1155M>>.

      - ***************************************************************************************

      - Smooth-rubbed, Grout-cleaned rubbed, SF-2.0, and SF-3.0 are concrete surface finishes that vary in appearance, cost, and application. Smooth-rubbed is achieved by rubbing green concrete with an abrasive stone to produce a clean, uniform surface—ideal for simple architectural elements where speed and cost-efficiency are priorities. Grout-cleaned rubbed involves applying a cement grout to fill surface voids and improve uniformity, making it suitable for exposed concrete with imperfections, though it’s more labor-intensive.

      - SF-2.0 is a moderate architectural finish requiring tighter formwork and consistent texture, commonly used for commercial buildings and visible structural elements where good appearance is needed without excessive cost. SF-3.0 is the highest-quality architectural finish, demanding precise formwork, minimal defects, and uniform color—best reserved for high-visibility or prestige projects like museums or civic buildings.

      - For most practical and cost-effective applications, SF-2.0 or Smooth-rubbed finishes are recommended, while Grout-cleaned rubbed and SF-3.0 are best when aesthetics are a top priority.

      - Retain the following paragraph if applicable. Choose the applicable option(s).

      - ***************************************************************************************

Provide formed concrete surfaces to be left exposed to view with ​<< smooth-rubbed finish;  Grout-cleaned rubbed finish;  Surface Finish-2.0; or  Surface Finish-3.0>>​.

      - ***************************************************************************************

      - SF-1.0 is a basic finish intended for non-architectural, utilitarian surfaces where appearance is not critical. It allows for visible formwork marks, minor surface voids, and minimal patching. It's commonly used in foundations, retaining walls, or hidden structural elements where cost and speed are prioritized over aesthetics.

      - Recommendation: Use SF-1.0 for structural or concealed elements to save on cost and labor. Choose SF-2.0 for visible concrete where a clean, consistent appearance is desired without the expense of high-end finishes like SF-3.0 or polished surfaces.

      - Retain the following paragraph if applicable. Choose the applicable option(s).

      - ***************************************************************************************

Provide formed concrete surfaces not exposed to view with ​<< Surface Finish-1.0; or  Surface Finish-2.0>>​.

      - ***************************************************************************************

      - For an overview of concrete flatwork finishing task, refer to the following ACI Certification – Concrete Flatwork Finishing video . For additional information, refer to How to Pour a Concrete Slab, Flatwork Finishing: Problems & Solutions and The Secret to Finishing Concrete.

      - Retain the following paragraph and applicable subparagraphs, as required by the project.

      - ***************************************************************************************

Finishing unformed surfaces (e.g., floors, sidewalks) as required by <<ACI SPEC-301>> Section 5.3.4.

Modify <<ACI SPEC-301>> Section 5.3.4.1 to read as follows

        - 5.3.4.1 Finisher qualifications—Unless EOR specifies additional requirements, at least one finisher or finishing supervisor shall be a certified ACI Flatwork Concrete Finisher/Technician or a certified ACI Flatwork Technician or equivalent.

        - ******************************************************************************

        - Retain the applicable subparagraphs from the following four.

        - ******************************************************************************

Wood-float surfaces which will receive tile with full bed setting system.

Steel trowel surfaces which will receive carpeting, resilient flooring, seamless flooring, or thin-set tile.

Broom finish surfaces of exterior walks, platforms, patios, ramps, parking structures and parking lots, unless otherwise indicated.

In areas with floor drains, maintain floor elevation at walls; slope surfaces uniformly to drains at 1/8 inch per foot, minimum.

CURING AND PROTECTION

      - ***************************************************************************************

      - For and overview of concrete curing refer to the following videos: Intro to curing concrete, Discover Curing - The Secret to Durable Concrete, Hot Weather Concrete, and Cold Weather Concrete.

      - ***************************************************************************************

General

Cure and protect concrete per <<ACI SPEC-301>> unless noted otherwise.

Measure and record concrete surface temperature using a LANL-approved method.

When using liquid membrane curing compounds, ensure compatibility with any subsequent protective coatings.

        - ******************************************************************************

        - ACI 318 Section 26.5.3.2(d) permits field-cured cylinders to be used to determine whether or not concrete in a structure has received adequate curing and protection.  If such is desired/required for the project (i.e., in lieu of/in addition to ‘full compliance’ with the ‘normal/typical’ curing and protection provisions) then the applicable ACI 318 provisions must be added herein per ACI 318 Section 26.5.3.1.

        - Per ACI 318 Section 26.5.3.2(a)–(c), the next subparagraph does not apply to high-early strength concrete, or to concrete that is cured using “accelerated curing.” Thus, if either of these apply to the project then this subparagraph must be edited accordingly.

        - ******************************************************************************

Curing

Concrete shall be maintained at a temperature of at least 50 degrees F (measured with a calibrated measuring device) and in a moist condition for at least the first 7 days after placement.

        - ******************************************************************************

        - Retain the following subparagraph if applicable.

        - ******************************************************************************

Cure high-early-strength concrete for a minimum of 3 days after placement.

Cure concrete in accordance with the applicable << "Unformed Concrete Surfaces"; or  "Formed Concrete Surfaces">> requirements << as applicable; or  None - N/A>>.

        - ******************************************************************************

        - Retain the following subparagraph if applicable.

        - ******************************************************************************

When permitted, and when curing duration is based on achieving specified in-place strength, terminate moisture retention measures only when one of the following conditions is met:

At least two 6 in. × 12 in. or three 4 in. × 8 in. field-cured cylinders, prepared per <<ASTM C31/C31M>>, achieve at least 70 percent of specified compressive strength (f′c) when tested per <<ASTM C39/C39M>>.

Laboratory-cured cylinders representative of in-place concrete exceed 85 percent of f′c, and in-place concrete temperature has been maintained at or above 50 degrees F during curing.

In-place concrete strength reaches f′c as verified by accepted test methods per <<ACI SPEC-301>> Section 2.3.4.2.

When one of the curing methods listed below under "Curing Methods" is used initially, it may be replaced after the concrete is 1 day old, provided that the concrete surface is never allowed to become dry.

        - ******************************************************************************

        - Retain the following subparagraph if applicable.

        - ******************************************************************************

For concrete containing silica fume, or when specified in the Contract Documents, select a curing method that supplies additional water throughout the curing period.

      - ***************************************************************************************

      - Retain the following paragraph if applicable.

      - ***************************************************************************************

Unformed concrete surfaces

If bleed water sheen is not visible after strikeoff and initial bull floating, begin initial curing by fogging, except during cold weather, or by applying an evaporation retarder. Use products such as MasterKure ER 50 or an equivalent until final curing begins.

Apply one of the curing methods listed below under "Curing Methods" immediately after finishing.

      - ***************************************************************************************

      - Retain the following paragraph if applicable.

      - ***************************************************************************************

Formed concrete surfaces

Keep absorbent wood forms continuously wet until removed.

After form removal, cure the exposed surfaces using one of the curing methods listed under "Curing Methods".

Curing methods: Unless otherwise specified, use one or more of the following methods to provide or preserve moisture:

Ponding, continuous fogging, or continuous sprinkling.

Application of continuously wet mats or fabric.

Continuous steam application (maximum temperature 150 degrees F).

Application of sheet materials

Application of a curing compound, as follows:

Apply as soon as the water sheen disappears and finishing is complete.

Follow manufacturer’s recommendations.

Apply in two coats at right angles.

Do not use curing compound on surfaces to receive bonded materials unless the compound does not interfere with bonding or will be completely removed.

        - ******************************************************************************

        - Retain the following subparagraph if applicable.

        - ******************************************************************************

Application of other EOR accepted curing methods.

Protection

Within 30 minutes after finishing, protect concrete from premature drying, extreme temperatures, and mechanical damage.

Maintain normal concrete above 50 degrees F and in a moist condition for at least 7 days.

Maintain high-early-strength concrete above 50 degrees F and in a moist condition for at least 3 days.

Concreting in Cold Weather

Cold weather exists when air temperature has fallen to, or is expected to fall below, 40 degrees F (4 degrees C) during the protection period as defined in <<ACI PRC-306>> Chapter 7.

When concrete must be placed in cold weather submit a detailed Cold-Weather Implementation Plan for EOR and LANL STR approval before beginning cold-weather concreting.

Provide adequate equipment for heating concrete materials and protecting concrete during freezing or near-freezing weather.

Frozen materials or materials containing ice shall not be used.

Forms, fillers, and ground which concrete will contact shall be free from frost and ice.

Select concrete materials and production methods so that the concrete temperature at delivery complies with the specified and/or indicated temperature limits.

Cold-Weather Implementation Plan (CWIP)

Refer to Appendix B for LANL guidance on the CWIP. Use this Appendix as an outline or starting point for preparing submittal.

Ensure the plan incorporates applicable recommendations from <<ACI PRC-306>> and includes worker safety requirements.

Include contingency procedures for abrupt weather changes and equipment failures.

Concreting in Hot Weather

Hot weather exists if the combination of temperature, humidity, and wind velocity is expected to cause a rate of evaporation equal to or greater than 0.2 pounds per square foot per hour.

When concrete placement is required during hot weather, or ambient daytime temperatures of 80 degrees F or higher at any time on the job site, prepare and submit a detailed Hot-Weather Implementation Plan for EOR and LANL STR approval.

Select concrete materials and production methods so that the concrete temperature at delivery complies with the specified and/or indicated temperature limits.

Handling, placing, protection, and curing procedures shall limit concrete temperatures or water evaporation that could reduce strength, serviceability, and durability of the member or structure.

Hot-Weather Implementation Plan (HWIP)

Refer to Appendix C for LANL guidance on the HWIP. Use this Appendix as an outline or starting point for preparing submittal.

Ensure the plan incorporates applicable recommendations from <<ACI PRC-305>> and includes worker safety requirements.

Include contingency procedures for abrupt weather changes and equipment failures.

FIELD QUALITY CONTROL

General Requirements

Coordinate concrete construction sequencing to allow for LANL Special Inspections in accordance with <<ICC (IBC)>> Chapter 17.

Provide 48-hour advance notice to schedule special inspections.

Provide a certified testing agency to perform field testing in accordance with <<ACI SPEC-301>>.

Testing agency certification shall be obtained through AASHTO or another nationally recognized accreditation service as permitted by <<ASTM C1077>>.

National accreditations must be specific to the facility and/or mobile unit performing the work.

Obtain EOR and LANL Building Official approval of the testing agency prior to performing any work. See LANL ESM Chapter 16 - Building Code Program for additional details and requirements.

Testing agencies performing concrete material testing shall comply with <<ASTM C1077>>.

Field testing of concrete shall be performed by an ACI Certified Concrete Field Testing Technician – Grade I.

Laboratory testing of concrete shall be done by ACI-Certified Concrete Laboratory Technician-Grade I or equivalent per <<ASTM C1077>>.

Notify LANL at least 48 hours in advance of field testing to allow for witnessing.

      - ***************************************************************************************

      - The EOR shall determine the frequency and type of field and laboratory testing per ACI 318 Section 26.12.2.

      - Notice that concrete strength is acceptable if (1) and (2) are satisfied: (1) the average of three consecutive tests equals or exceeds f’c and (2) no strength test falls below f’c by more than 500 psi if f’c is 5000 psi or less; or by more than 0.1f’c if f’c exceeds 5000 psi, for additional details refer to ACI 318 Section 26.12.3.1.

      - To ensure that enough strength tests are available to calculate the moving average required by acceptance criteria (1) above, ACI 318 Section 26.12.2.1(b) requires that on a given project “…strength test specimens shall be made from at least five randomly selected batches or from each batch if fewer than five batches are used.” However, per ACI 318 Section 26.12.2.1(c): strength test is not required for small pours (i.e., less than 50 cubic yards of a given concrete mix), if evidence of satisfactory strength is submitted to and approved by the LBO. Such evidence should be in terms of historical compression strength data for the concrete mix being used (at least 15 strength tests) demonstrating that criteria (1) and (2) are satisfied.

      - ***************************************************************************************

Frequency of Testing

Obtain samples for measuring fresh concrete properties from each truckload selected for strength testing.

Take random samples for preparing strength-test specimens in accordance with (a) through (c)

At least once per day.

At least once for each ​​<< 50;  100; or  _______>>​​ cubic yards of concrete placed.

At least once for each << 5000; or  _______>> square feet of surface area of slabs or walls.

          - **********************************************************************

          - Omit the following subparagraph if historical compressive strength data (at least 15 strength tests) is available for the concrete mix being used, demonstrating compliance with ACI 318-19, Section 26.12.3.1.

          - **********************************************************************

Strength test specimens shall be made from at least five randomly selected batches or from each batch if fewer than five batches are used.

A strength test shall be the average of:

Two cylinders (6 in. × 12 in.), or

Three cylinders (4 in. × 8 in.),

Made from the same sample and tested at 28 days or the designated test age for determining f′c.

Laboratory-Cured Specimens

Mold and cure cylinders in accordance with <<ASTM C31/C31M>>

Provide the on-site curing container and verify that cylinders are maintained in accordance with <<ASTM C31/C31M>>.

Number of cylinders: minimum << four>> 6-inch diameter by 12-inch tall, or << six>> 4-inch diameter by 8-inch tall.

Field-Cured Specimens

LANL may require field-cured cylinders to verify adequacy of curing and protection.

Cure field-cured cylinders in accordance with <<ASTM C31/C31M>>.

Number of cylinders: minimum ​<< four>>​ 6-inch diameter by 12-inch tall, or ​<< six>>​ 4-inch diameter by 8-inch tall.

Mold field-cured cylinders at the same time and from the same sample as laboratory-cured cylinders.

Acceptance Testing Procedures

Take samples for acceptance testing at the discharge point of the transit mixer into a wheelbarrow, per <<ASTM C172/C172M>>, unless concrete is placed using pumps or conveyors.

When pumps or conveyors are used, take samples at the end of the pipe or final conveyor belt at the point of placement. Follow <<ACI PRC-304.2>>​​​​​​​​​​​​ for pumping of concrete and<<ACI PRC-304.4>> for belt conveying.

Perform the following tests whenever concrete strength-test specimens are taken:

Sample concrete in accordance with <<ASTM C172/C172M>> .

Record temperature of concrete in accordance with <<ASTM C1064/1064M>>.

Perform slump test in accordance with <<ASTM C143/C143M>>.

Perform air content test in accordance with <<ASTM C231/C231M>> pressure method.

Perform density testing in accordance with <<ASTM C138/C138M>> when required by <<ASTM C94/C94M>>.

Prepare strength-test cylinders in accordance with ​<< the paragraph titled "Laboratory-Cured Specimens".; or  the paragraphs titled "Laboratory-Cured Specimens" or "Field-Cured Specimens", as applicable.>>​

Strength Testing and Cylinder Pickup

Test strength-test cylinders in accordance with <<ASTM C39/C39M>> at << 7; or  _______>> days and << 28; or  _______>> days, minimum.

        - ******************************************************************************

        - The default 24-hour period for collecting strength-test cylinders at the lower end of the pickup window should not be used without careful evaluation. This is because premature handling of cylinders, before the concrete has adequately set, may lead to low strength results. The 24-hour timeframe was originally chosen based on field experience with pre-approved extended-set concrete mixes.

        - ASTM C31, Section 11 states that, “Specimens shall not be transported until at least 8 h after final set.” Design and Control of Concrete Mixtures, 15th Ed., PCA, states, “Typically, initial setting occurs between 2 and 6 hours after batching and final setting occurs between 4 and 12 hours.” However, these requirements/observations apply to typical mixtures without hydration controlling admixtures (e.g., MasterSet Delvo) or SCMs (e.g., pozzolan).

        - ******************************************************************************

Strength test cylinders must be picked-up at the job site between 24 and 48 hours after molding.*

        - * Evaluate the 24-hour minimum pickup time based on the mixture design and field conditions. Do not pick up cylinders before the concrete has set sufficiently to prevent reduced strength results.

Obtain approval from the LANL Chief Inspector before picking up cylinders earlier than 24 hours.

Comply with <<ASTM C94/C94M>> and <<ASTM C31/C31M>>​ for initial curing requirements and times.

CONCRETE ACCEPTANCE CRITERIA

General

Conform to the requirements of this Section and <<ACI SPEC-301>>, and <<ACI CODE-318>>, as applicable.

Reject re-tempered concrete.

Reject concrete that exceeds the design placement time, as specified under Placement Time and Drum Revolution Counter under PART 3 Article PLACING CONCRETE.

Comply with the testing, sampling, and sample preparation requirements under PART 3 Article FIELD QUALITY CONTROL.

Field Acceptance of Fresh Concrete

Concrete Temperature: Unless otherwise specified in the approved Hot-Weather or Cold-Weather Implementation Plans: Maximum 95 degrees F, Minimum 55 degrees F at the time of placement.

Slump: Comply with <<ASTM C94/C94M>> Section 7.

Place concrete with slump below the specified minimum only when the LANL inspector determines that the concrete is workable and can be consolidated by vibration.

Do not place low-slump concrete due to exceeding time limits or other nonconforming conditions.

The LANL inspector will note the low slump in the inspection report but will not generate an NCR unless the concrete strength report indicates that it is unacceptable.

        - ******************************************************************************

        - High air-content beyond the specified range becomes a factor that can impact strength but not durability.

        - ******************************************************************************

Air content: Comply with <<ASTM C94/C94M>> Section 8.

          - The LANL inspector will note the high air-content in the inspection report but will not generate an NCR unless the concrete strength report indicates that it is unacceptable.

Workability and Uniformity: Concrete shall be visibly uniform, without segregation, excessive bleeding, or other signs of nonconformance.

Non-Conforming Fresh Concrete Properties

Reject any load with fresh concrete properties outside specified tolerances unless adjustment is explicitly permitted by this Section and the approved mix design.

Document all adjustments, including amount, time, revised test results, and retesting.

Retest adjusted loads; reject any loads that fails to meet acceptance criteria after permitted adjustments.

If systematic trends of marginal or non-conforming fresh properties occur, suspend placement and investigate plant operations, mix proportions, and batching/transport equipment before resuming.

      - ***************************************************************************************

      - Mixes incorporating pozzolan cement replacement typically show higher long-term strength (90 days) and an initial slower strength gain than for regular mixes without pozzolan. Pozzolan mixes typically show that the compressive strength at 28 days with pozzolan cement replacement is between 80% and 95% of the strength without replacement.

      - ***************************************************************************************

Acceptance of concrete strength

Compressive strength test results (standard-cured specimens) shall be evaluated in accordance with <<ACI CODE-318>> acceptance criteria.

Strength for each class of concrete is satisfactory when both of the following conditions are met:

Every arithmetic average of any three consecutive strength tests equals or exceeds f’c

No individual strength test (average of two 6×12 in. or three 4×8 in. cylinders) falls below f′c by more than:

500 psi when f′c ≤ 5000 psi, or

10 percent of f′c when f′c > 5000 psi.

Strength tests used for acceptance shall be:

Properly sampled, molded, cured, and tested per the requirements under PART 3 Article FIELD QUALITY CONTROL.

Traceable to specific placements in the structure.

Non-Conforming Strength Test Results

Immediately notify the EOR and LANL STR of any non-conforming strength or hardened property test results.

Increase testing frequency for the affected mix and placement area as directed.

Perform additional testing as required, which may include:

Field-cured cylinders.

Core tests from the structure per applicable ACI and ASTM procedures.

Non-destructive testing (NDT), where appropriate.

The EOR, in consultation with LANL STR, shall evaluate structural adequacy, durability, and serviceability using available test data and analysis.

Disposition of non-conforming concrete may include:

Acceptance as-is based on structural evaluation.

Corrective measures or strengthening.

Partial or total removal and replacement.

Appearance

Concrete surfaces shall be free of honeycombs, embedded debris, and dimensional variances.

Appearance shall conform to the requirements of this Section, <<ACI SPEC-301>>, and referenced standards.

Construction requirements

Conform to the lines, details, dimensions, and tolerances specified for construction.

Functional and Durability Requirements

The completed structure shall provide required:

Strength and stiffness under all applicable load combinations.

Durability for specified exposure categories (F, S, W, C) and service life.

            - *************************************************************

            - Retain the following subparagraph if required by the project.

            - *************************************************************

Watertightness where required (e.g., tanks, vaults).

Where leakage, excessive deflection, vibration, or other performance deficiencies occur, corrective measures shall be implemented per approved repair procedures and subcontractor QAP requirements.

DEFECTIVE CONCRETE

      - ***************************************************************************************

      - For large structural repairs, submit a detailed repair procedure/specification through Appendix A – Design Change(s). The submittal must include the following:

        - Description of the damage and extent of deterioration.

        - Scope/Applicability: Define applicable repair types (e.g., deep honeycomb, shallow-to-medium patches). Demolition and removal procedures, Surface preparation method(s), Placement method (e.g., form-and-pour, shotcrete, hand patching).

        - Application Type: Specify whether the repair is formed or unformed.

        - Approved Repair Materials: List all approved materials for each repair type.

        - Temperature Limits: State acceptable temperature ranges for material placement.

        - Placement Notes: Include specific instructions for material handling and placement.

        - Curing Requirements: Detail curing methods and durations.

        - QA Acceptance Criteria: Define measurable quality standards, criteria and or requirements for acceptance of completed repairs. Include an inspection and testing plan to verify compliance.

        - Required Hold Points: Identify inspection and approval stages before proceeding.

        - Schedule and sequencing of the repair work.

        - Engineering justification for the proposed method, if deviating from original design intent.

      - Refer to the following documents for additional guidance on large structural concrete repairs:

        - ICRI 030130 Guide specifications structural concrete repair

        - UFGS 03 0100 – Rehabilitation of Concrete

        - SpecLink 03 0100 – Maintenance of Concrete

        - ACI SPEC-563 – Repair of Concrete in Buildings—Specification

        - Five Star Design-a-Spec – Structural Concrete

        - ACI 548.15 – Specification for Crack Repair by Epoxy Injection

        - ACI 546.3R Guide for the Selection of Materials for the Repair of Concrete

        - ACI PRC-546 Concrete Repair—Guide

        - ACI Field Guide to Concrete Repair Application Procedures and the videos at ACI Repair Application Procedures and Case Studies

      - ***************************************************************************************

Defective concrete is concrete not conforming to PART 3 Article CONCRETE ACCEPTANCE CRITERIA.

The LANL Building Official may classify concrete as defective if placement does not comply with Part 3, Article CURING AND PROTECTION, due to potential durability issues.

Consider pre-approved 4000 psi, 4500 psi, and 5000 psi extended mix designs defective if not placed within 2-1/4 hours after initial mixing.

Do not accept or place defective concrete. Return fresh defective concrete to the supplier.

Replace defective concrete that does not meet strength criteria at the Subcontractor’s expense.

The Subcontractor may evaluate in-place strength by testing at least three core samples from each affected area in accordance with <<ACI CODE-318>>, <<ACI SPEC-301>>, and <<ASTM C42>>. Fill core holes in accordance with <<ACI SPEC-301>>.

      - ***************************************************************************************

      - Use ACI 301 guidelines for cosmetic or nonstructural surface repairs. Select repair materials specified in ACI 301 or listed in Section ​<< 03 6000 - Grouting>>​. If using materials from Section ​<< 03 6000 - Grouting>>​, be aware that the repaired surface may not visually match the existing in-situ concrete. Per ACI 301-16, 5.2.1.6 Surface Repair Materials — "Unless otherwise specified, use repair mortar for surface defects. For exposed concrete, repair mortar shall match the color of the adjacent concrete." For additional details refer to ACI 301-16 Section 5.3.7.3 Repair of surface defects other than tie holes

      - ***************************************************************************************

Replace defective concrete that does not meet appearance criteria at the Subcontractor’s expense. The LANL STR may permit repair at the Subcontractor’s expense.

Repair or replace concrete that does not conform to lines, details, dimensions, tolerances, or other construction requirements at the Subcontractor’s expense.

Replace, repair, or test concrete with potential durability deficiencies, including concrete that does not conform to Part 3, Article CURING AND PROTECTION, at the Subcontractor’s expense.

If testing is performed to verify durability, use <<ASTM C457>>.

Accept the concrete for moderate exposure when the average air-void spacing factor (Ḹ) does not exceed 0.008 inches and no single value exceeds 0.010 inches. Otherwise, replace the concrete at the Subcontractor’s expense.

END OF MAIN SECTION; APPENDICES FOLLOW

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

  - THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

  - THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 03 3001, REV. 20, DATED APRIL 15, 2026.

    - APPENDIX A: DESIGN CHANGES

      - ***************************************************************************************

      - NOTE: Edit Design Changes Table A1 template for each project. In doing so, the specifier must add job-specific requirements. Brackets are used in the text to indicate designer choices or locations where text must be supplied by the designer. Once the choice is made or text is supplied, remove the brackets. Some assistance is provided in this regard through the use of author notes embedded in Table A1. However, in order to comply with this requirement, the “Foreword to checklists” in ACI 301 must be understood and followed-through (since the vast majority of the tabulated items have ACI 301 as the source).

      - For “Work not specified” in/by ACI 301 (e.g., heavyweight shielding concrete, shotcrete, self-consolidating concrete, etc.), the main body of this Section requires editing, and related items must be added to the following table.

      - ***************************************************************************************

      - Subcontractor shall prepare a Field Change Request (FCR) for each item listed in the Design Change(s) Table A1, as necessary/if applicable. When a submittal requires review to oversee FCR implementation (e.g., procurement, procedure, or request review), the FCR should also modify the 01 3300 Att. A submittal log to include the same.

      - Subcontractor shall provide each FCR to the LANL STR within the timeframe noted in the “timeframe” column to the right of the tabulate item. The timeframes may be adjusted for individual projects by Subcontract or the LANL STR. The LANL STR will request the review and approval of the EOR and any other authority and notify the Subcontractor after approval is granted for each FCR.

      - In addition, for new mix designs, the Subcontractor must schedule and manage any sub-tiers to ensure that the proper approach and scheduling is used to obtain all necessary approvals and tests of concrete constituents that make up the new mix designs.

      - ***************************************************************************************

      - Retain and edit the following two paragraphs and five subparagraphs as required by the project.

      - ***************************************************************************************

      - The FCR reviews should be generally consistent with the following schedule:

        - << 2>> days for the LANL STR to give the FCR to the Design Agency

<< 10>> days for the Design Agency to approve the FCR.

<< 2>> days for the LANL STR to return the approved FCR.

<< 5–10>> days for the Subcontractor to act on the approval.

<< 5>> days for the Subcontractor to correct any FCR for re-review followed by a << 5>> days review period.

      - (The complete process will take approximately << 5>> weeks if the FCR is not returned unapproved).

      - Note 1: Design-build Subcontractors shall obtain their EOR approval before providing an FCR to the LANL STR (differs from 3rd bullet in schedule above).

      - Note 2: The term “engineer-of-record (and EOR)” is synonymous with the term “architect/engineer (i.e., as applicable to project in question).”

      - Note 3: The term “Subcontract Documents” includes the set of documents prepared by the EOR as the basis for construction; these documents contain subcontract forms, subcontract conditions, Specifications, Drawings, addenda, and subcontract changes.

      - Note 4: Source: Requirement source is <<ACI SPEC-301>><< -20>> unless noted otherwise.

      - TABLE A1 Design Change(s)

      - All FCRs and review comments (from LANL and/or EOR) should be retained in files for future reference during the Work.

      - In the event of a conflict between the items listed below and related ones that appear on the Construction Drawings, contact the LANL STR. As necessary, review the Source of an indicated item(s) for additional detail.

      - General requirements

        - ****Source: ACI 301 Section 1.8.1.4****

Proposed repair methods, materials, and modifications to the Work (if/when completed concrete work is found to be noncompliant with Subcontract Documents). Within 3 work days of “finding”

        - ****Source: ACI 301 Section 1.8.4.2(e)****

Description of repair to be performed to bring potentially under-strength concrete into compliance with Subcontract Documents. Within 3 work days of “finding”

        - ****Source: ACI 301 Section 1.8.5.2(e) ****

Description of repair work performed to bring nondurable concrete into compliance with Subcontract Documents. Within 3 work days of “finding”

        - ****Source: PART 1 Article QUALITY ASSURANCE****

Identification of any “as-found/as-received” out-of-tolerance devices, and description of where and how the device(s) was used. Within 3 work days of “finding”

      - ***************************************************************************************

      - Retain the following paragraph and applicable subparagraphs, as required by the project.

      - ***************************************************************************************

Formwork and formwork accessories

        - ****Review the items listed pertaining ACI 301 Sections 2.1.2.1 and 2.1.2.2 and omit those that are not applicable to project. ****

        - ****Source: ACI 301 Section 2.1.2.1(a)****

Data on form-facing materials (if different from that specified in 2.2.1.1). 1 month before formwork installation.

        - ****Refer to ACI 228.1R for recommendations on developing suitable correlation data. Source: ACI 301 Sections 2.1.2.1(c), 2.3.4.2****

Correlation data on alternative methods of determining concrete strength for formwork removal. 1.5 months before formwork installation.

        - ****Source: ACI 301 Section 2.2.1.2****

Request to use ferrous ties with breakback less than 3/4 in. 1 month before formwork installation.

        - ****Source: 2.2.1.6****

Alternative material or size (to those specified or permitted), or both, for chamfer strips. 1 month before formwork installation.

        - ****Source: ACI 301 Section 2.2.2.3****

Request to use earth cuts as form for vertical or sloping surfaces. 1 month before formwork installation.

        - ****Source: ACI 301 Sections 2.2.2.5(a), 2.1.2.1(b)****

Alternative locations and details for construction, isolation, expansion, and contraction joints (if different than those indicated in Subcontract Documents). 1.5 months before formwork installation.

        - ****Source: ACI 301 Section 2.2.2.5(c)****

Alternative keyways locations and details (if different than those indicated in Subcontract Documents). 1.5 months before formwork installation.

        - ****Source: ACI 301 Section 2.2.2.5(d)****

Alternative waterstop locations and details (if different than those indicated in Subcontract Documents). 1.5 months before formwork installation.

        - ****Source: ACI 301 Section 2.3.2.4****

Request to remove formwork at a lower compressive strength than specified compressive strength for removal of forms. 1.5 months before formwork installation.

      - ***************************************************************************************

      - Retain the following paragraph if applicable.

      - ***************************************************************************************

Reinforcement and reinforcement supports

        - ****Source: ACI 301 Section 3.1.2.1(c)****

Request to use splices not indicated in Subcontract Documents.1 month before reinforcement placement.

        - ****Source: ACI 301 Section 3.1.2.1(d)****

Request to use mechanical splices* not indicated in Subcontract Documents. 1 month before reinforcement placement.

        - An ICC-ESR, or comparable, for the splice product shall accompany the request, and must indicate that the product complies with the Project Code of Record.

        - ________________________

        - * Includes typical proprietary splicing/coupling systems, as well as Form Saver, and Cadweld.

        - ****Source: ACI 301 Section 3.1.2.1(e)****

Request for placement of column dowels without using templates. 15 work days before reinforcement placement.

        - ****Source: ACI 301 Section 3.1.2.1(f), 3.3.2.8****

Request and procedure to field-bend or straighten reinforcing bars partially embedded in concrete at locations not indicated in Subcontract Documents. 15 work days before reinforcement placement.

        - ****Source: ACI 301 Section 3.2.2.2(a) and PART 1 Article QUALITY ASSURANCE****

Request to weld reinforcing bar; and description of reinforcing bar weld locations, welding procedure specifications, and welder qualifications. 15 work days before welding.

          - **********************************************************************

          - Retain the following subparagraph and applicable sub-subparagraphs when welding, brazing or joining is required.

          - Choose the applicable option(s) in the following subparagraph.

          - **********************************************************************

Per the requirements of ​​​​​<< Section 01 4444 - Offsite Welding, Brazing and Joining Requirements; and  Section 01 4455 - Onsite Welding, Brazing and Joining Requirements>>​​​​​, submit:

            - *************************************************************

            - When offsite only, omit submittals below regarding onsite welding. For high-risk applications such as ML-1 or ML-2, add submittals for “Weld Filler Material Control Procedures” and “Filler Material Certified Material Test Reports (CMTRs)” when required. Add “Post-Weld Heat Treatment Procedures” when required.

            - For Onsite welding use of LANL WPS/PQR is the default; coordinate usage with the LANL CWI; no submittal required.

            - For Onsite, welders are tested by LANL who will produce WPQR and track continuity; this includes brazing, bonding, and fusing; no submittal required.

            - *************************************************************

Welding Procedure Specification (WPS) and supporting Procedure Qualification Record (PQR).

Welder Performance Qualification Records (WPQR) including continuity.

Weld Filler Material Control Procedure for ML-1 and ML-2 applications.

Filler Material Certified Material Test Reports (CMTRs) for ML-1 and ML-2 applications.

Post-Weld Heat Treatment Procedures (where applicable).

Shop drawings with weld details/symbols.

          - **********************************************************************

          - Retain the following paragraph and applicable subparagraphs when NDE is required for the project. ​

          - **********************************************************************

Per the requirements of Section ​​​<< 01 4525 - Non-Destructive Examination (NDE) Requirements>>​​​, submit:

Inspector qualification records.

Written Practice or Procedure for Qualification and Certification of NDE Personnel

NDE Personnel Qualification Records

NDE Procedures

NDE Procedure Qualification Records (when required by code)

NDE Report(s)

Inspection procedures.

For other than <<ASTM A706/A706M>> reinforcing bar, CMTR of the reinforcing bar material properties that demonstrate conformance to the requirements of <<AWS D1.4/D1.4M>>.

        - ****Source: ACI 301 Section 3.1.2.1(h)****

Request to field-cut reinforcement, including location and type of bar to be cut and reason field cutting is required. 15 work days before cutting.

        - ****Source: ACI 301 Section 3.1.2.1(i)****

Proposed supports for coated reinforcement and materials for fastening coated reinforcement not covered in <<ACI SPEC-301>> Section 3.3.2.4. 15 work days before reinforcement placement.

        - ****Source: ACI 301 Section ****

Request to relocate reinforcement beyond the specified placing tolerances (to avoid interference with other reinforcement, conduits, or embedded items). Submit resulting reinforcement arrangement. 1 month before reinforcement placement.

        - ****Source: ACI 301 Sections 3.1.2.1(g), 3.2.1.2(b)****

Inspection and quality-control program of plant applying epoxy coating if plant is not certified by Concrete Reinforcing Steel Institute (CRSI) Epoxy Coating Plant Certification Program. 1 month before planned shipment date.

        - ****Source: ACI 301 Section 3.2.1.2(b)****

Provide certification program, equivalent to that of CRSI-certified plant, for non-CRSI-certified plant applying epoxy coating for evaluation by EOR. 1 month before planned shipment date.

        - ****Source: ACI 301 Section 3.2.1.8****

Request to use of alternative reinforcement support types. 15 work days before reinforcement placement.

        - ****Source: ACI 301 Section 3.2.2.1****

Request to heat reinforcement before bending. 15 work days before reinforcement placement.

Concrete mixtures

Pre-Approved Standard Mix Designs

          - ****Source: ACI 301 Section 4.2.2.5(b)****

Request to deliver concrete at a temperature exceeding 95 degrees F. 10 work days before placement

        - ******************************************************************************

        - Retain the following subparagraph if applicable.

        - Omit If only a Standard Mix(es) will be used on/by the Project

        - ******************************************************************************

Alternative Mix Designs

          - ****Source: ACI 301 Sections 4.1.2.8, 4.2.3.5, and 4.2.3.6****

Requests for adjustments to mixture proportions. Requests to adjust mixture proportions necessary for workability or consistency. 15 work days before use in a placement.

          - ****Source: ACI 301 Section 4.1.2.11, 4.3.1.2 ****

Request to use the volumetric batching and proposed method. 15 work days before the initial placement.

          - ****Source: ACI 301 Section 4.2.1.1****

Requests to use other than <<ASTM C150/C150M>> Type I or Type II cement. When <<ASTM C595/C595M>> or <<ASTM C1157/C1157M>> hydraulic cements are used for sections of the structure that are assigned Exposure Class F3, verify compliance of the concrete with <<ACI SPEC-301>> Table 4.2.1.1(b). 15 work days before the initial placement.

          - ****Source: ACI 301 Section 4.2.1.6****

Request to use admixtures.15 work days before the initial placement.

          - ****Source: ACI 301 Section 4.2.1.8****

Request to change materials and data verifying that properties of the concrete mixture conform to the requirements of <<ACI SPEC-301>> Section 4.2.2. 15 work days before the initial placement.

          - ****Source: ACI 301 Section 4.2.2.1****

Request to use a slump other than that specified.10 work days before placement.

          - ****Source: ACI 301 Section 4.2.2.5(b)****

Request to deliver concrete at a temperature exceeding 95 degrees F. 10 work days before placement.

          - ****Source: ACI 301 Section ****

Handling, placing, and constructing.

        - ****Source: ACI 301 Section 5.1.2.2(d)****

Request for placement of concrete in hot weather with a temperature exceeding that specified and/or indicated. 2 work days before placement.

        - ****Source: ACI 301 Section 5.1.2.3(a)****

Proposed location and treatment of construction joints not indicated in Subcontract Documents, including method for surface preparation and achieving bond.5 work days before beginning ‘jointing’.

        - ****Source: ACI 301 Section 5.1.2.3(b)****

Proposed location of movement joints not indicated in Subcontract Documents.5 work days before beginning ‘jointing’.

        - ****Source: ACI 301 Sections 5.1.2.2(j), 5.3.6 and PART 3 Article CURING AND PROTECTION****

Request to use, and proposed methods of, curing other than those of <<ACI SPEC-301>> Section 5.3.6 or PART 3 Article CURING AND PROTECTION. 5 work days before placement.

        - ****Source: ACI 301 Section 5.1.2.2(k)****

Surface repair materials: specification data, methods of use, and application procedure for proposed material to repair surface defects other than site-mixed Portland-cement mortar described in <<ACI SPEC-301>> Sections 5.2.1.6 and 5.37. 5 work days before placement.

        - ****Source: ACI 301 Sections 1.8.1.3, 1.8.1.4, 1.8.1.5****

Repair of rejected concrete: submit applicable repair material specification, manufacturer’s data on the proposed repair material, and proposed preparation and application procedure. 5 work days before placement.

        - ******************************************************************************

        - Retain the following subparagraph if applicable.

        - Do not retain 5.3.2.3(c) if Pre-Approved mixes will be used on/in the Project (since these are ‘pumpable’ mixes; hence, “alternative mixture” not necessary/applicable). If other mixes will be used, do not retain if modification of them is not/will not be permitted.

        - ****Source: ACI 301 Section 5.3.2.3(c)****

        - ******************************************************************************

When permitted, alternative mixture for pumped concrete. 5 work days before placement.

        - ****Source: ACI 301 Sections 5.1.2.1(j), 5.3.5****

Sawed joints in slabs: Submit request to saw joints in slabs or cut reinforcement at sawn joints in a manner that is not indicated in Contract Documents. Refer to <<ACI PRC-302.1>> for further guidance. 5 work days before beginning ‘jointing’.

        - Source: ACI 301 Section 5.3.6.1 5.3.6.6(a)

Request to use shorter curing duration, or if a curing method other than that specified is desired. 5 work days before placement.

        - ****Source: ACI 301 Section 5.3.7.3****

Submit alternative method for repair of surface defects other than tie holes, for details refer to <<ACI SPEC-301>> Section 5.3.7.3. 5 work days before placement.

    - APPENDIX B: COLD-WEATHER IMPLEMENTATION PLAN (CWIP)

      - SUBMITTAL DEVELOPMENT GUIDANCE

      - PART 1 Article Submittals in this Section requires the Subcontractor to submit a CWIP, based on this document and <<ACI PRC-306>>, at least 5 work days1 before placement in cold weather*. The purpose of the CWIP submittal is to ensure cold-weather concreting is performed properly and safely.

      - ________________________

      - 1One (1) day/work day is one 24-hour period.

      - * “Cold weather” is defined in <<ACI PRC-306>>​, Section 2.2.

      - The level of detail provided in the CWIP is key. Including inadequate detail will result in rejection of the submittal, but including too much detail can unduly limit options. The CWIP should simply describe the means and methods (based on the recommendations in <<ACI PRC-306>>) intended to be used in order to ensure cold-weather concreting is performed properly and safely. The CWIP should not include items or activities that the Subcontractor is not prepared to perform; since, once it is approved by the engineer of record and LANL, the CWIP provides a written record of the Subcontractor’s commitments/intentions.

      - Introduction

      - Introduce the CWIP with a statement like the following:

        - This Cold Weather Implementation Plan (CWIP) is submitted as required by this Section and conforms to the requirements therein, to include the following definition of cold weather:

        - "Cold weather exists when the air temperature has fallen to, or is expected to fall below, 40 degrees F (4 degrees C) during the protection period; protection period is defined as the time recommended to prevent concrete from being affected by exposure to cold weather during construction."

        - By following this CWIP, concrete placed during cold weather will develop the indicated and/or specified strength and durability.

      - Additional detail on “protection period” is provided below under “Protection against less-than-permissible temperatures.”

      - Production

      - Discuss the details of cold weather concrete production with the concrete Provider. If they have a written plan they’re willing to share, include the applicable portions of it in the CWIP. Describe how the minimum and maximum concrete temperatures in <<ACI PRC-306>> Table 5.12 will be met. Heated mixing water, aggregates, or both are typically used.

      - Note: The use of means other than, or in addition to, heated mixing water and aggregate (e.g., use of increased cement content, accelerating admixtures, cold-weather admixture systems, rapid-setting cements, etc.) could constitute a “change of materials (per <<ACI SPEC-301>> Section 4.2.1.63).” Also, this Section prohibits the use of calcium chloride (as an admixture).

      - ________________________

      - 2The word “maintained” in Line 1 of <<ACI PRC-306>> Table 5.1 applies to the “protection period.”

      - 3<<ACI SPEC-301>> Section 4.2.1.6 requires that admixtures used shall be the same as those used in trial mixtures or in the concrete represented by submitted field test records.

      - Preparation and Transportation

      - Describe how the subgrade will be protected from frost and, if frozen, how it will be thawed*; and how reinforcement and forms will be protected from accumulation of ice or snow (prior to concrete placement). In some cases, covering the subgrade with insulating material for a few days will protect it from frost/freezing. In other cases it may be necessary to apply heat to the subgrade followed by insulation. Provide specifics on the use of insulation and/or heat and its duration.

      - * Thawed subgrade shall be re-compacted.

      - Generally, concrete can be produced at a high enough temperature at the plant, thus no special methods are needed to insulate the concrete truck drum. If the concrete will be placed by crane and bucket, pumping, or conveyor, very low air temperatures may necessitate steps to ensure that the placement temperature does not drop below the allowable minimum. Scheduling deliveries that reduce truck waiting time (i.e., as much as possible given that the LANL Vehicle Access Portals can be potential choke points) is the least expensive way of achieving this goal. Discuss the aforementioned topics, as applicable, in the CWIP, and relate temperature measurements (i.e., of the air and/or the concrete prior to placement) to the action to be taken if the placement temperature falls below the allowable minimum.

      - Finally, indicate in the CWIP the temperature range (in degrees Fahrenheit) stipulated by the EOR that the as-delivered concrete must be within, and that provisions will be made in advance of concrete placement to protect it against less-than-permissible temperatures without drying of concrete.

      - Protection against less-than-permissible temperatures

      - The “protection period,” or the time in terms of days, begins as soon as possible after placement, consolidation, and finishing*. The duration of the “protection period” (recommended to prevent concrete from being adversely affected by exposure to “cold weather” during construction) is indicated in <<ACI PRC-306>> Table 7.2. Equipment, materials, and methods used to maintain concrete placed during “cold weather” at the recommended temperature given in Line 1 of <<ACI PRC-306>> Table 5.1 and for the length of time in Table 7.2 include insulating materials, heaters, enclosures, and internal heating (or a combination of these).

      - If insulating materials are to be used, ensure the required type(s) and amount(s) needed to provide the R-value(s) indicated in <<ACI PRC-306>> Tables 9.3 will be on hand. On a related note, if quick cycling of forms is a possibility, the R-value of insulating material by itself (vs. that with formwork in place) may have to be relied on for some/much of the protection period (i.e., for the concrete affected by quick form cycling).

      - If heaters are to be used**, ensure direct-fired ones are properly vented and not used to directly heat the surface of concrete.

      - If an enclosure(s) is to be used, ensure the materials needed to build it will be on hand: plastic sheeting, lumber, vents, hardware, and (perhaps) heaters.

      - If internal heating is to be used, ensure moisture retention and temperature control are addressed in the CWIP.

      - ________________________

      - * When finishing flatwork, if bleed water is present, wait until it evaporates, or skim it off using a rope, hose, or squeegee before troweling.

      - ** Prior to the use of flame-producing items in technical areas with Weapons Facility Operations (WFO), acquire a spark/flame permit, and/or written approval from the Facility Operations Director (FOD).

      - Describe in CWIP the means and methods of “protection” that will be used. And, if the project includes multiple types of concrete elements that would be affected by “cold weather” differently (e.g., slabs on grade vs. elevated slabs, interior walls vs. exterior walls, etc.), this description must have a commensurate level of detail. Describe how concrete temperature during placement being no higher than 20 degrees F more than the minimum temperature values in <<ACI PRC-306>> Table 5.1 will be ensured. Finally, as applicable, describe worker- and fire-safety measures that will be implemented.

      - Temperature monitoring

      - Indicate in the CWIP how weather conditions (i.e., air temperature, sun exposure, humidity, and wind conditions) and concrete temperature (i.e., at time of delivery and after it’s placed) will be monitored in order to determine and prepare the necessary protective measures, or to revise them. Describe in the CWIP where and how concrete temperatures (at least on the surface if not internally, too*) will be monitored and recorded at the point of placement. <<ACI PRC-306>> recommends measuring concrete temperature at regular intervals to ensure the effectiveness of the provided protection. Indicate the general locations of temperature-measuring devices having an accuracy of ± 2 degrees F** and the frequency with which the temperature measurements will be taken. Describe information to be included in temperature records as indicated in <<ACI PRC-306>>, Section 4.4.

      - ________________________

      - * Internal temperature monitoring is recommended by <<ACI PRC-306>>. Therefore, if such monitoring is not performed, the CWIP must provide the reasoning.

      - ** All temperature-measuring devices shall be calibrated.

      - At the end of the “protection period,” <<ACI PRC-306>> recommends a gradual decrease in surface temperature to minimize thermal stresses that might cause cracking. Thus, indicate in the CWIP how the concrete will be allowed to cool such that the maximum allowable temperature drop in the first 24 hours after the end of “protection period’ (in Line 5 of <<ACI PRC-306>> Table 5.1) isn't exceeded.

      - Curing

      - Describe in the CWIP how prevention of concrete-surface desiccation (e.g., evaporation of moisture, extreme drying, etc.) will be accomplished. This description will account for curing after the “protection period” and, if an enclosure is used, curing during the “protection period.” Also, describe how curing conditions will be such that the recommended minimum concrete temperatures in <<ACI PRC-306>> Table 5.1 are not exceeded by more than 20 degrees F.

      - Water curing is discouraged if concrete will be exposed to freezing temperatures (unless additional protection measures are used) because a high moisture content renders the concrete vulnerable to freezing. Insulating materials serve the dual purpose of keeping the concrete warm and preventing moisture loss. Leaving wood forms in place is effective for walls and columns. Indicate if curing compounds will be used.

      - Abrupt changes in weather and backup equipment and materials

      - Indicate the weather service(s) that will be monitored in order to stay abreast of potential local weather changes. Describe how concrete will be protected from unexpected freezing (i.e., periods that don’t qualify as “cold weather”). Indicate the backup materials and equipment that will be on hand in the case of breakdowns. Finally, having a procedure for installing “emergency construction joints” in the CWIP could prove to be beneficial.

      - Additional detail on most of the topics discussed herein (e.g., production, preparation, protection, temperature monitoring, and curing) can be found in <<ACI PRC-306>>.

    - APPENDIX C: HOT-WEATHER IMPLEMENTATION PLAN (HWIP)

      - SUBMITTAL DEVELOPMENT GUIDANCE

      - PART 1 Article Submittals in this Section requires the Subcontractor to submit a HWIP, based on this document and <<ACI PRC-305>>, at least 5 work days1 before placement in hot weather.* The purpose of the HWIP submittal is to ensure hot-weather concreting is performed properly and safely.

      - The level of detail provided in the HWIP is key. Including inadequate detail will result in rejection of the submittal, but including too much detail can unduly limit options. The HWIP should simply describe the means and methods (based on the recommendations in <<ACI PRC-305>>) intended to be used in order to ensure hot-weather concreting is performed properly and safely. The HWIP should not include items or activities that the Subcontractor is not prepared to perform; since, once it is approved by the engineer-of-record (EOR) and LANL, the HWIP provides a written record of the Subcontractor’s commitments/intentions.

      - ________________________

      - 1One (1) day/work day is one 24-hour period.

      - * “Hot weather” is defined in this Section, PART 3 Article Curing and Protection.

      - Introduction

      - Introduce the HWIP with a statement like the following:

        - This Hot Weather Implementation Plan (HWIP) is submitted as required by this Section and conforms to the requirements therein, to include the following definition of hot weather:

        - "Hot weather exists if the combination of temperature, humidity, and wind velocity is expected to cause a rate of evaporation equal to or greater than 0.2 pounds per square foot per hour at the time of concrete placement."

        - By following this HWIP, concrete placed during hot weather will develop the indicated and/or specified strength and durability.

      - Production and Delivery

      - Discuss the details of hot-weather concrete production with concrete provider. If they have and share a written plan, include the applicable portions of it in the HWIP. Describe how the concrete temperature will be reduced and controlled. Refrigerated mixing water, replacement of some mixing water with ice, shading and/or wetting the aggregate stockpile, are typically used.

      - Note: The use of means other than, or in addition to, cooled mixing water and aggregate (e.g., use of decreased cement content, increased supplementary cementitious materials, set-retarding admixtures, water-reducing admixtures, extended set-control admixtures, etc.) could constitute a “change of materials (per <<ACI SPEC-301>> Section 4.2.1.62).”

      - Since delays and prolonged agitation/mixer revolutions lead to higher concrete temperatures and slump loss, schedule deliveries that reduce truck waiting time (i.e., as much as possible given that the LANL Vehicle Access Portals can be potential choke points). Ensure that the rate of delivery is manageable given the available crew to place, finish and cure the concrete; also, ensure the availability of placement and finishing equipment, and protection. If/when possible, schedule around the most favorable weather conditions (i.e., day and time of day). Discuss these topics in the HWIP.

      - Finally, indicate in the HWIP the temperature range (in degrees Fahrenheit) stipulated by the EOR that the as-delivered concrete must be within.

      - ________________________

      - 2Section 4.2.1.6 requires that admixtures used shall be the same as those used in trial mixtures or in the concrete represented by submitted field test records.

      - Preparation for placing and curing

      - Discuss specific measures that will be taken in preparation for concrete placement. Examples of such measures are as follows:

        - Moistening the subgrade3, and fogging forms and reinforcement prior to placing concrete.

        - Having all forms, equipment, and workers ready to handle concrete.

        - Erecting/installing temporary sunscreens and windbreaks.

        - Ensuring mixers, chutes, pump lines and other equipment in contact with the concrete are shaded, covered with wet burlap, or painted white.

      - Indicate in the HWIP how weather conditions (i.e., air temperature, sun exposure, humidity, and wind speed) and concrete temperature (i.e., at time of delivery and after it’s placed) will be monitored* in order to determine and prepare the necessary protective measures, or to revise them. And, if the air temperature could drop 40 degrees F or more within the same day, indicate how the concrete will be protected from thermal shock.4

      - Also, indicate the backup materials and equipment that will be on hand in the case of breakdowns. An example of backup equipment is at least one (1) standby vibrator for every three (3) in use.

      - ________________________

      - * All monitoring/measuring devices shall be calibrated.

      - 3 Ensure there’s no free water (i.e., don’t allow excessive water to pond).

      - 4 Refer to this Section, Appendix B for thermal protection guidance.

      - Protection against moisture loss

      - The goal is to protect the concrete from moisture loss during the placing and curing periods. Examples of such protection include covering with moisture-retaining material such as wet burlap, plastic sheeting or liquid-membrane curing compound;5 and evaporation retardants.

      - Describe in HWIP the means and methods of protection that will be used to protect against moisture loss. And, if the project includes multiple types of concrete elements that would be affected by this differently (e.g., flatwork vs. formed concrete), this description must have a commensurate level of detail.

      - ________________________

      - 5Using white-pigmented membrane curing compounds will help with proper coverage and reflect heat from the surface.

      - Placement and finishing

      - Place and consolidate the concrete as quickly as possible. The same goes for finishing; however, do not begin a finishing operation if the concrete isn’t ready. For example, for flatwork, don’t begin finishing if there’s still  bleed water on the surface, and don’t begin final finishing until water sheen has disappeared (from the surface). Also, regarding flatwork, take special precautions when finishing slabs on grade placed directly on vapor retarders.6

      - In discussing placement and finishing in the HWIP, if applicable, differentiate between formed concrete and flatwork.

      - ________________________

      - 6Refer to NRMCA’s Concrete in Practice (CIP) 29 for details.

      - Curing and protection

      - Immediately following final finishing, protect the concrete (from low humidity, drying winds, and large ambient temperature differential) and start the curing process. Cure continuously for at least seven (7) days with water or with another method per <<ACI PRC-308>>7.

      - Guard against rapid cooling of concrete (i.e., more than 5 degrees F per hour, or more than 50 degrees F per day, during the first day) with a least dimension of less than 12 inches and/or that obtains high strength at an early age. If applicable, indicate in the HWIP how such concrete will be gradually cooled.

      - In addition to discussing the aforementioned topics in the HWIP, if applicable, indicate the differences in means and methods associated with curing and protecting formed concrete versus flatwork.

      - ________________________

      - 7Refer to Section 3.7 of <<ACI PRC-308>> for acceptable hot-weather curing methods.

      - Testing and inspection

      - Make slump and air-content tests, and strength-test cylinders immediately after obtaining the concrete sample.

      - Protect test cylinders at the jobsite to maintain temperature (i.e., 60–80 degrees F for f’c < 6,000 psi) and moisture for initial curing. For example, cast cylinders in plastic molds with a plastic lid (or cover them with plastic sheeting), don’t leave them unprotected in direct sunlight, provide field-curing boxes with ice or refrigeration8, submerge them in water inside an insulated cooler(s)/ bucket(s) with a lid(s), etc.

      - Inspection (i.e., quality control vs. quality assurance/special inspection) is necessary to ensure the HWIP is executed and adhered to thoroughly.

      - Discuss testing and inspection in the HWIP.

      - Additional detail on all the topics discussed herein can be found in <<ACI PRC-305>>.

      - ________________________

      - 8Refer to NRMCA’s CIP 9 and 34 for additional details.

- END OF SECTION