Section 03 4100 
Precast Structural Concrete

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 4 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., SECTION INCLUDES in PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Structural POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable sections from all Divisions, especially Division 1, General Requirements.

      - Section is developed for pre-fabricated reinforced structural concrete for ML-4 projects. For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality sections.

      - Subcontractor (and Sub-Tier) must ensure that this specification is followed and that required documentation is available before fabrication begins.

  - *************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

      - ***************************************************************************************

      - Retain the applicable paragraphs from the following.

      - ***************************************************************************************

Precast structural concrete.

Precast structural concrete with commercial architectural finish.

Post-tensioned precast structural concrete

Mold Materials

Reinforcing Materials

Prestressing Tendons

Concrete Materials

Steel Connection Materials

Stainless-Steel Connection Materials

Bearing Pads

Grout Materials

Ducts

Reveal and Accent Strips

Insulated Flat-Wall Panel Accessories

Concrete Mixtures

RELATED REQUIREMENTS

Section ​​<< 01 4444 - Offsite Welding, Brazing and Joining Requirements>>​​.

Section ​<< 01 4455 - Onsite Welding, Brazing and Joining Requirements>>​.

Section << 01 4525 - Non-Destructive Examination (NDE) Requirements>>.

      - ***************************************************************************************

      - The applicable edition/version of a given code or standard shall be either the latest one or the one referenced by the versions of ICC (IBC) and ACI 318 that apply to the Project.

      - Codes and Standards that are referenced within the tabulated codes and standards shall be considered applicable to this Project.

      - ***************************************************************************************

REFERENCE STANDARDS

AASHTO LRFDCONS - LRFD Bridge Construction Specifications.

AASHTO M 251M/M 251 - Standard Specification for Plain and Laminated Elastomeric Bridge Bearings.

ACI PRC-213 - Guide for Structural Lightweight-Aggregate Concrete.

ACI SPEC-117 - Specification for Tolerances for Concrete Construction and Materials.

ACI SPEC-301 - Specifications for Concrete Construction.

ACI 306.1 - Standard Specification for Cold Weather Concreting.

ACI CODE-318 - Building Code for Structural Concrete—Code Requirements and Commentary.

ACI ITG-7 - Specification for Tolerances for Precast Concrete.

ACI PRC-211.1 - Selecting Proportions for Normal-Density and High Density-Concrete - Guide.

ASTM A27/A27M - Standard Specification for Steel Castings, Carbon, for General Application.

ASTM A36/A36M - Standard Specification for Carbon Structural Steel.

ASTM A47/A47M - Standard Specification for Ferritic Malleable Iron Castings.

ASTM A108 - Standard Specification for Steel Bar, Carbon and Alloy, Cold-Finished.

ASTM A123/A123M - Standard Specification for Zinc (Hot-Dip Galvanized) Coatings on Iron and Steel Products.

ASTM A153/A153M - Standard Specification for Zinc Coating (Hot-Dip) on Iron and Steel Hardware.

ASTM A184/A184M - Standard Specification for Welded Deformed Steel Bar Mats for Concrete Reinforcement.

ASTM A276/A276M - Standard Specification for Stainless Steel Bars and Shapes.

ASTM A283/A283M - Standard Specification for Low and Intermediate Tensile Strength Carbon Steel Plates.

ASTM A307 - Standard Specification for Carbon Steel Bolts, Studs, and Threaded Rod 60 000 PSI Tensile Strength.

ASTM A416/A416M - Standard Specification for Low-Relaxation, Seven-Wire Steel Strand for Prestressed Concrete.

ASTM A500/A500M - Standard Specification for Cold-Formed Welded and Seamless Carbon Steel Structural Tubing in Rounds and Shapes.

ASTM A563/A563M - Standard Specification for Carbon and Alloy Steel Nuts (Inch and Metric).

ASTM A572/A572M - Standard Specification for High-Strength Low-Alloy Columbium-Vanadium Structural Steel.

ASTM A615/A615M - Standard Specification for Deformed and Plain Carbon-Steel Bars for Concrete Reinforcement.

ASTM A666/A666M - Standard Specification for Annealed or Cold-Worked Austenitic Stainless Steel Sheet, Strip, Plate, and Flat Bar.

ASTM A675/A675M - Standard Specification for Steel Bars, Carbon, Hot-Wrought, Special Quality, Mechanical Properties.

ASTM A706/A706M - Standard Specification for Deformed and Plain Low-Alloy Steel Bars for Concrete Reinforcement.

ASTM A722/A722M - Standard Specification for High-Strength Steel Bars for Prestressed Concrete.

ASTM A767/A767M - Standard Specification for Zinc-Coated (Galvanized) Steel Bars for Concrete Reinforcement.

ASTM A775/A775M - Standard Specification for Epoxy-Coated Steel Reinforcing Bars.

ASTM A780/A780M - Standard Practice for Repair of Damaged and Uncoated Areas of Hot-Dip Galvanized Coatings.

ASTM A882/A882M - Standard Specification for Filled Epoxy-Coated Seven-Wire Steel Prestressing Strand.

ASTM A884/A884M - Standard Specification for Epoxy-Coated Steel Wire and Welded Wire Reinforcement.

ASTM A910/A910M - Standard Specification for Uncoated, Weldless, 2-Wire and 3-Wire Steel Strand for Prestressed Concrete.

ASTM A924/A924M - Standard Specification for General Requirements for Steel Sheet, Metallic-Coated by the Hot-Dip Process.

ASTM A1064/A1064M - Standard Specification for Carbon-Steel Wire and Welded Wire Reinforcement, Plain and Deformed, for Concrete.

ASTM B633 - Standard Specification for Electrodeposited Coatings of Zinc on Iron and Steel.

ASTM C33/C33M - Standard Specification for Concrete Aggregates.

ASTM C42/C42M - Standard Test Method for Obtaining and Testing Drilled Cores and Sawed Beams of Concrete.

ASTM C109/C109M - Standard Test Method for Compressive Strength of Hydraulic Cement Mortars (Using 50 mm [2 in.] Cube Specimens).

ASTM C144 - Standard Specification for Aggregate for Masonry Mortar.

ASTM C150/C150M - Standard Specification for Portland Cement.

ASTM C260/C260M - Standard Specification for Air-Entraining Admixtures for Concrete.

ASTM C330/C330M - Standard Specification for Lightweight Aggregates for Structural Concrete.

ASTM C404 - Standard Specification for Aggregates for Masonry Grout.

ASTM C494/C494M - Standard Specification for Chemical Admixtures for Concrete.

ASTM C567/C567M - Standard Test Method for Determining Density of Structural Lightweight Concrete.

ASTM C578 - Standard Specification for Rigid, Cellular Polystyrene Thermal Insulation.

ASTM C591 - Standard Specification for Unfaced Preformed Rigid Cellular Polyisocyanurate Thermal Insulation.

ASTM C595/C595M - Standard Specification for Blended Hydraulic Cements.

ASTM C618 - Standard Specification for Coal Ash and Raw or Calcined Natural Pozzolan for Use in Concrete.

ASTM C666/C666M - Standard Test Method for Resistance of Concrete to Rapid Freezing and Thawing.

ASTM C881/C881M - Standard Specification for Epoxy-Resin-Base Bonding Systems for Concrete.

ASTM C979/C979M - Standard Specification for Pigments for Integrally Colored Concrete.

ASTM C989/C989M - Standard Specification for Slag Cement for Use in Concrete and Mortars.

ASTM C1017/C1017M - Standard Specification for Chemical Admixtures for Use in Producing Flowing Concrete.

ASTM C1077 - Standard Practice for Agencies Testing Concrete and Concrete Aggregates for Use in Construction and Criteria for Testing Agency Evaluation.

ASTM C1107/C1107M - Standard Specification for Packaged Dry, Hydraulic-Cement Grout (Nonshrink).

ASTM C1218/C1218M - Standard Test Method for Water-Soluble Chloride in Mortar and Concrete.

ASTM C1240 - Standard Specification for Silica Fume Used in Cementitious Mixtures.

ASTM D412 - Standard Test Methods for Vulcanized Rubber and Thermoplastic Elastomers--Tension.

ASTM D2240 - Standard Test Method for Rubber Property--Durometer Hardness.

ASTM E165/E165M - Standard Practice for Liquid Penetrant Testing for General Industry.

ASTM E329 - Standard Specification for Agencies Engaged in Construction Inspection, Testing, or Special Inspection.

ASTM E709 - Standard Guide for Magnetic Particle Testing.

ASTM F436/F436M - Standard Specification for Hardened Steel Washers Inch and Metric Dimensions.

ASTM F593 - Standard Specification for Stainless Steel Bolts, Hex Cap Screws, and Studs.

ASTM F844 - Standard Specification for Washers, Steel, Plain (Flat), Unhardened for General Use.

ASTM F3125/F3125M - Standard Specification for High Strength Structural Bolts and Assemblies, Steel and Alloy Steel, Heat Treated, Inch Dimensions 120 ksi and 150 ksi Minimum Tensile Strength, and Metric Dimensions 830 MPa and 1040 MPa Minimum Tensile Strength.

AWS C5.4 - Recommended Practices for Stud Welding.

AWS D1.1/D1.1M - Structural Welding Code - Steel.

AWS D1.4/D1.4M - Structural Welding Code - Steel Reinforcing Bars.

ICC (IBC) - International Building Code.

LANL ESM - LANL Engineering Standards Manual STD-342-100.

LANL TSM - LANL Tailored Standards Manual (TSM) STD-342-600.

MIL-DTL-882F - Cloth, Duck, Cotton or Cotton-Polyester Blend, Synthetic Rubber, Impregnated, and Laminated, Oil Resistant.

MIL-P-21035B - Paint High Zinc Dust Content, Galvanizing Repair (Metric).

MPI #79 - Primer, Alkyd, Anti-Corrosive for Metal.

PCI MNL-116 - Manual for Quality Control for Plants and Production of Structural Precast Concrete Products.

PCI MNL-120 - PCI Design Handbook.

PCI MNL-123 - Connections Manual: Design and Typical Details of Connections for Precast and Prestressed Concrete.

PCI MNL-124 - Design for Fire Resistance of Precast Prestressed Concrete.

PCI MNL-127 - Erector's Manual: Standards and Guidelines for the Erection of Precast Concrete Products.

PCI MNL-135 - Tolerance Manual for Precast and Prestressed Concrete Construction.

PCI TR-6 - Guidelines For The Use Of Self-Consolidating Concrete In Precast/Prestressed Concrete.

PTI TAB.1 - Post-Tensioning Manual.

SSPC-PA 1 - Shop, Field, and Maintenance Coating of Metals.

SSPC-Paint 20 - Zinc-Rich Coating (Type I - Inorganic, and Type II - Organic).

SSPC-SP 3 - Power Tool Cleaning.

DEFINITIONS

For definitions and acronyms, refer to COE Glossary of Terms.

      - ***************************************************************************************

      - Retain this paragraph if a design reference sample has been preapproved by EOR for precast structural concrete units with architectural finish.

      - ***************************************************************************************

Design Reference Sample:  Sample of approved precast structural concrete color, finish, and texture, preapproved by EOR.

COORDINATION

Furnish loose connection hardware and anchorage items to be embedded in or attached to other construction before starting that Work.  Provide locations, setting diagrams, templates, instructions, and directions, as required, for installation.

ACTION SUBMITTALS

Product Data:  For each type of product indicated.

Design Mixtures:  For each precast concrete mixture. Include compressive strength and water-absorption tests.

Shop Drawings: Include member locations, plans, elevations, dimensions, shapes and sections, openings, support conditions, and size, location, and types of reinforcement, including special reinforcement. Detail fabrication and installation of precast structural concrete units.

        - ******************************************************************************

        - Omit subparagraphs below not applicable to Project.

        - ******************************************************************************

Indicate joints, reveals, and extent and location of each surface finish.

Indicate separate face and backup mixture locations and thicknesses.

Indicate welded connections by AWS standard symbols. Show size, length, and type of each weld.

Detail loose and cast-in hardware, lifting and erection inserts, connections, and joints.

Indicate locations, tolerances, and details of anchorage devices to be embedded in or attached to structure or other construction.

Indicate tendon profile, supports and locations, and clearances required for jack.

Indicate magnitude and location of prestressing forces.

Include and locate openings larger than by << 10 inches>>.

Indicate individual piece mark for each precast structural concrete unit (even if unit is not unique).

Indicate location of each precast structural concrete unit by same identification mark placed on panel.

Indicate relationship of precast structural concrete units to adjacent materials.

Indicate estimated camber for precast floor slabs with concrete toppings.

Indicate shim sizes and grouting sequence.

Indicate locations and details of pickup points for precast structural concrete units

​<< Insert additional drawing detail>>​.

      - ***************************************************************************************

      - Retain the following paragraph and applicable subparagraphs when welding, brazing or joining is required. Coordinate with procedures for welder certification below in PART 1 Article QUALITY ASSURANCE.

      - ***************************************************************************************

Per the requirements of ​​​​​​<< Section 01 4444 - Offsite Welding, Brazing and Joining Requirements; and  Section 01 4455 - Onsite Welding, Brazing and Joining Requirements>>​​​​​​, submit

        - ******************************************************************************

        - When offsite only, omit submittals below regarding onsite welding. For high risk applications such as ML-1 or ML-2, add submittals for “Weld Filler Material Control Procedures” and “Filler Material Certified Material Test Reports (CMTRs)” when required.  Add “Post-Weld Heat Treatment Procedures” when required.

        - For Onsite welding use of LANL WPS/PQR is the default; coordinate usage with the LANL CWI; no submittal required.

        - For Onsite, welders are tested by LANL who will produce WPQR and track continuity; this includes brazing, bonding, and fusing; no submittal required.

        - ******************************************************************************

Welding Procedure Specification (WPS) and supporting Procedure Qualification Record (PQR).

Welder Performance Qualification Records (WPQR) including continuity.

Inspector qualification records

Inspection procedures

Shop drawings with weld details/symbols

      - ***************************************************************************************

      - Retain the following paragraph and applicable subparagraphs when NDE is required for the project.

      - ***************************************************************************************

Per the requirements of Section ​​​​<< 01 4525 - Non-Destructive Examination (NDE) Requirements>>​​​​, submit:

Inspector qualification records.

Inspection procedures.

      - ***************************************************************************************

      - If either or both of the next two (2) paras. and subparagraphs apply, edit for project specificity. Omit paragraphs and subparagraphs that are not applicable.

      - ***************************************************************************************

For each part of the precast-concrete structure not designed by the licensed design professional responsible for precast concrete (or the person to whom precast-concrete design has been delegated), state the required minimum compressive strength for the following stages of construction:

Precast concrete: At stripping from the forms, and during handling, shipping and erection<< .; or  ; and>>

Precast, prestressed concrete: At transfer of prestress, at stripping from the forms, and during handling, shipping and erection<< .; or  ; and,>>

<< _______>>.

For post-tensioned precast structural concrete, submit to the licensed design professional responsible for precast concrete (or the person to whom precast-concrete design has been delegated) the type, size, details and location of post-tensioning anchorages not shown.

      - ***************************************************************************************

      - Retain the following paragraph and applicable subparagraphs, as required by the project. Choose the applicable option in the following paragraph.

      - ***************************************************************************************

Samples: ​<< Required.;  Not required.;  _______; or  None - N/A>>​

        - ******************************************************************************

        - If precast units require a finish treatment, include a sample submission illustrating color and finish. Coordinate with sample panels below in PART 1 Article QUALITY ASSURANCE.

        - ******************************************************************************

Samples:  Submit ​<< two; or  ____>>​ ​<< _________>>​, ​<< ____by____ inch>>​ in size, illustrating surface finish treatment.

        - ******************************************************************************

        - Retain first subparagraph below if architectural finishes, colors, and textures are preselected, specified, or scheduled.  Coordinate with sample panels below in PART 1 Article QUALITY ASSURANCE.

        - ******************************************************************************

For each type of finish indicated on exposed surfaces of precast structural concrete units with architectural finish, in sets of 3, illustrating full range of finish, color, and texture variations expected; approximately ​<< 12 by 12 by 2 inches>>​.

Where other faces of precast concrete unit are exposed, include Samples illustrating workmanship, color, and texture of backup concrete as well as facing concrete.

        - ******************************************************************************

        - Retain the following subparagraph if additional samples are required.

        - ******************************************************************************

<< _______>>

      - ***************************************************************************************

      - The option to specify shop drawings &/or calculations that pertain to temporary bracing & shoring comes from ACI 301.  Retain 1st option below, and 1st subparagraph, if erection won’t pose a hazard to LANL employees or the general public.  Retain 2nd option, and 2nd & 3rd subparas., if LANL employees or the general public will be located, or have access, within a distance of twice the panel height to be erected.

      - ***************************************************************************************

Provide handling procedures, and ​​<< erection plan.; or  PE-stamped erection plan, and calculations that provide the technical basis for what is shown on the erection plan.>>​​

The erection plan shall include erection sequences, tolerances on the vertical and horizontal alignment of temporary braces, and the procedure for field modifications. If temporary bracing will require use of deadmen, such anchors shall be permanent (i.e., not relocatable/ reusable).

The erection plan shall include shop drawings for temporary bracing and shoring, erection sequences, bracing plan, tolerances on the vertical and horizontal alignment of temporary braces, and the procedure for field modifications. If temporary bracing will require use of deadmen, such anchors shall be permanent (i.e., not relocatable/ reusable).

The calculations shall include the design for temporary connections, temporary bracing, and the sequence of completing connections. The design loads for temporary braces shall be in accordance with the << LANL TSM; or  LANL ESM>>. Finally, temporary braces shall be designed with an additional 50 percent margin against failure (i.e., increase loads, or decrease member capacity, by a factor of 1.5 above and beyond what the << LANL TSM; or  LANL ESM>> require).

      - ***************************************************************************************

      - Retain "Delegated-Design Submittal" Paragraph below if design services have been delegated to Subcontractor.

      - ***************************************************************************************

Delegated Design Submittal:  For precast structural concrete indicated to comply with the performance requirements and design criteria, the comprehensive engineering design including analysis data, signed and sealed by the qualified Professional Engineer responsible for their preparation.

      - ***************************************************************************************

      - Retain the following paragraph if required by the project.

      - ***************************************************************************************

Fire resistance calculations.

      - ***************************************************************************************

      - Retain the following paragraphs and applicable subparagraphs, if required by the project.

      - ***************************************************************************************

Sustainable Design Submittals

LEED Submittals:

Product Data: For products having recycled content, documentation indicating percentages by weight of postconsumer and pre-consumer recycled content. Include statement indicating cost for each product having recycled content.

          - **********************************************************************

          - Retain "Design Mixtures for Credit ID 1" Subparagraph below if fly ash, ground granulated blast-furnace slag, silica fume, or other materials are used as Portland cement replacements for LEED-NC, LEED-CS, or LEED for Schools Credit ID 1.  To achieve this credit, replacement materials must be substituted for at least 40 percent of the Portland cement that would otherwise be used.

          - **********************************************************************

Design Mixtures for Credit ID 1: For each concrete mixture containing fly ash as a replacement for Portland cement or other Portland cement replacements and for equivalent concrete mixtures that do not contain Portland cement replacements.

Product Data: For adhesives and sealants, including printed statement of VOC content.

INFORMATIONAL SUBMITTALS

      - ***************************************************************************************

      - Coordinate first paragraph below with qualification requirements in Section << 01 4000 - Quality Requirements - Non-Nuclear>> and as supplemented below in PART 1 Article QUALITY ASSURANCE.

      - ***************************************************************************************

Qualification Data: For << installer;  fabricator;  testing agency; and  _______>>.

      - ***************************************************************************************

      - Retain paragraph below for material certificates from manufacturers.

      - ***************************************************************************************

Manufacturer’s Material Certificates: For the following, from manufacturer:

        - ******************************************************************************

        - Revise list below to suit Project.

        - ******************************************************************************

Cementitious materials.

<< Reinforcing materials;  prestressing tendons; and  _______>>.

Admixtures.

Bearing pads.

<< Structural-steel shapes;  hollow structural sections; and  _______>>.

<< _______>>.

      - ***************************************************************************************

      - Retain paragraph below for material test reports that are Subcontractor's responsibility.

      - Note that PCI MNL 116 requires aggregates conform to several standards and outlines which tests should be included in material test reports.

      - ***************************************************************************************

Material Test Reports: Certified suppliers test reports for aggregates.

      - ***************************************************************************************

      - Retain paragraph below if Subcontractor is responsible for source quality-control testing.

      - ***************************************************************************************

Source quality-control reports.

Field quality-control reports.

      - ***************************************************************************************

      - Retain paragraph below if project includes prestressed concrete.

      - ***************************************************************************************

Jack Calibration Records (in accordance with <<PCI MNL-116>>, Section 5.2.7).

Closeout Submittals

        - ******************************************************************************

        - Retain one or both of the following subparagraphs if applicable.

        - ******************************************************************************

Maintenance Data: For precast structural concrete ​​<< with Commercial Architectural Finish; or  None - N/A>>​​.

Project Records: Including jacking and tensioning records.

Warranties

Submit copy of the Precast Structural Concrete manufacturer’s warranty covering materials.

Submit copy of the Precast Structural Concrete warranty covering workmanship.

      - ***************************************************************************************

      - Retain the following Article, as required by the project.

      - ***************************************************************************************

DESIGN CHANGE

Submit design changes through a Field Change Request (FCR) for Engineer of Record (EOR) approval.

QUALITY ASSURANCE

      - ***************************************************************************************

      - LANL ESM, IBC & ACI 301 distinguish between quality control (QC) and quality assurance (QA):

      - -     QC is what is contained herein, & is the responsibility of the Construction        Subcontractor (i.e., fabricator & erector).

      - -     QA (which is required by IBC Ch, 17) is contained in the EOR’s            Statement of Special Inspections (SSI), & is the responsibility of LANL      (i.e., execution of the SSI). The SSI template is found in LANL ESM Chapter 16 - Building Code Program, Section IBC-IP, Attach. B.

      - ***************************************************************************************

Fabricator Qualifications: A firm that assumes responsibility for engineering precast structural concrete units to comply with performance requirements. Responsibility includes preparation of Shop Drawings and comprehensive engineering analysis by a qualified professional engineer.

        - ******************************************************************************

        - Usually retain first subparagraph below and select category to qualify a fabricator.  A precast concrete plant certified to produce products in Category C2A, for example, is also certified to produce products in Categories C1, C1A, and C2 but not in Category C3, C3A, C4, or C4A.  See PCI’s website, www.pci.org, for discussion of PCI's Groups C and CA categories.

        - ******************************************************************************

Participates in PCI's Plant Certification program​<< at time of bidding; or  None - N/A>>​ and is designated a PCI-certified plant as follows:

          - **********************************************************************

          - Retain first subparagraph and appropriate option if Group C products without architectural finishes are required.  Retain second subparagraph and appropriate option if Group CA products with architectural finishes are required.

          - **********************************************************************

<< Category C1 - Precast Concrete Products (no prestressed reinforcement);  Category C2 - Prestressed Hollowcore and Repetitively Produced Products;  Category C3 - Prestressed Straight Strand Structural Members; or  Category C4 - Prestressed Deflected Strand Structural Members>>.

          - *** OR ***

Group CA, << Category C1A - Precast Concrete Products (no prestressed reinforcement).;  Category C2A - Prestressed Hollowcore and Repetitively Produced Products.;  Category C3A - Prestressed Straight-Strand Structural Members.; or  Category C4A - Prestressed Deflected-Strand Structural Members.>>

      - ***************************************************************************************

      - At the time of publication of this Section, Rev. 0 there were no PCI Certified erectors in or near NM. Therefore, installation must be performed by an installer that is qualified per the following paragraph.

      - ***************************************************************************************

Installer Qualifications: An experienced precast concrete erector who, before erection of precast concrete, has retained a "PCI-Certified Field Auditor" to conduct a field audit of a project installed by erector in << Category S1 - Simple Structural Systems; or  Category S2 - Complex Structural Systems>> and who produces an Erectors' Post Audit Declaration, according to <<PCI MNL-127>>.

Testing Agency Qualifications: Qualified according to <<ASTM C1077>> and <<ASTM E329>> for testing indicated. Testing Agency must be pre-approved by the LANL. This includes any use of testing agencies by sub-tier suppliers, fabricators, etc. Current listing is with LANL ESM Chapter 16 - Building Code Program.

Design Standards: Comply with <<ACI CODE-318>> and design recommendations in <<PCI MNL-120>><< , and PTI TAB.1; or  None - N/A>>, applicable to types of precast structural concrete units indicated.

      - ***************************************************************************************

      - Edit the following if more restrictive tolerances are required by project, or if one or more the cited documents don’t address tolerances applicable to project.

      - ***************************************************************************************

Quality-Control Standard: For manufacturing procedures and testing requirements, and for quality-control recommendations, comply with <<PCI MNL-116>>. For dimensional tolerances of members, comply with <<ACI ITG-7>>. For interfacing tolerances for precast concrete with cast-in-place concrete, comply with <<ACI SPEC-117>>.

      - ***************************************************************************************

      - Retain "Welding Qualifications" Paragraph below if shop or field welding is required. Coordinate the with the “WPQR” paragraph in the PART 1 Article Action Submittals, above. Select the applicable option and retain the appropriate subparagraph(s) where additional shop and/or field welding requirements apply.

      - ***************************************************************************************

Welder Qualifications:  Welding processes and welding operators qualified in accordance with << AWS D1.1/D1.1M; and  AWS D1.4/D1.4M>> and dated no more than << 12 months; or  ______>> before start of scheduled welding work. << Comply with the following additional requirements:; or  None - N/A>>

Shop: Refer to Section << 01 4444 - Offsite Welding, Brazing and Joining Requirements>>

Field: Refer to Section << 01 4455 - Onsite Welding, Brazing and Joining Requirements>>

      - ***************************************************************************************

      - Consider retaining paragraph below for precast structural concrete units with architectural finish. PCI recommends review of pre-production sample panels to establish range of finish, color, and texture to be expected.  Revise number and size of sample panels in paragraph to suit Project.

      - ***************************************************************************************

Sample Panels: After sample approval and before fabricating precast structural concrete units<< with architectural finish; or  None - N/A>>, produce a minimum of << 2; or  ______>> sample panels approximately << 16 sq. ft; or  ______>> in area for review by EOR. Incorporate full-scale details of architectural features, finishes, textures, and transitions in sample panels.

Locate panels where indicated or, if not indicated, as directed by EOR.

Damage part of an exposed-face surface for each finish, color, and texture, and demonstrate adequacy of repair techniques proposed for repair of surface blemishes.

After approval of repair technique, maintain one sample panel at fabricator's plant and one at Project site in an undisturbed condition as a standard for judging the completed Work.

Demolish and remove sample panels when directed.

      - ***************************************************************************************

      - Consider retaining paragraph below for precast structural concrete units with architectural finish.  Omit if sample panels in paragraph above will suffice and added expense of mockups is not required.

      - ***************************************************************************************

Mockups: After sample panel approval but before production of precast structural concrete units<< with architectural finish; or  None - N/A>>, construct full-sized mockups to verify selections made under sample submittals and to demonstrate aesthetic effects and set quality standards for materials and execution.

        - ******************************************************************************

        - Revise or include three subparagraphs below to suit Project.

        - ******************************************************************************

Build mockup as indicated on Drawings including​<< sealants,;   inserts,;  _______; and  None - N/A>>​ precast structural concrete units with an architectural finish complete with anchors, connections, flashings, and joint fillers.

        - ******************************************************************************

        - Retain subparagraph below if mockups are not only for establishing appearance factors.

        - ******************************************************************************

Approval of mockups does not constitute approval of deviations from the Subcontract Documents contained in mockups unless EOR specifically approves such deviations in writing.

        - ******************************************************************************

        - Retain subparagraph below if mockups are installed as part of building rather than erected separately.

        - ******************************************************************************

Approved mockups may become part of the completed Work if undisturbed at time of Substantial Completion.

      - ***************************************************************************************

      - Retain the following paragraph if required by the project.

      - ***************************************************************************************

Welding: Welding of reinforcing bars will be permitted only with the approval of the LANL Welding Program SME. Utilize a procedure that is approved by the EOR and this SME prior to start of work.

      - ***************************************************************************************

      - Retain paragraph below if Work of this Section is extensive or complex enough to justify a preinstallation conference.

      - ***************************************************************************************

Preinstallation Conference:  Conduct conference at << Project site; or  _______>>.

DELIVERY, STORAGE, AND HANDLING

Support units during shipment on non-staining shock-absorbing material in same position as during storage.

Store units with adequate bracing and protect units to prevent contact with soil, to prevent staining, and to prevent cracking, distortion, warping or other physical damage.

Store units with dunnage across full width of each bearing point unless otherwise indicated.

Place adequate dunnage of even thickness between each unit.

Place stored units so identification marks are clearly visible, and units can be inspected.

Handle and transport units in a position consistent with their shape and design in order to avoid excessive stresses that would cause cracking or damage.

Lift and support units only at designated points shown on Shop Drawings.

PART 2 - PRODUCTS

    - **********************************************************************************************

      - Retain this article and one of two options below if naming fabricators.  See PCI's magazine "Ascent" or its Web site, www.pci.org, for current PCI-certified plant listings.

    - **********************************************************************************************

MANUFACTURERS

Fabricators: Subject to compliance with requirements, ​​<< provide products by one of the following; or  available fabricators offering products that may be incorporated into the Work include, but are not limited to, the following>>​​:

Coreslab Structures, 2800 2nd St.  Sch. P.O. Box 1609, Albuquerque, NM 87103 (505)-247-3725.

Ferreri Concrete Structures Inc., 6151 Chappell Rd., Albuquerque, NM 87113, (505)-344-8823.

Castillo Prestress, 6 Lopez Loop, Belen, NM 87002, (505)-864-0238.

<< _______>>.

      - ***************************************************************************************

      - Retain the following Article, along with applicable paragraphs and subparagraphs, as required by the project.

      - ***************************************************************************************

PERFORMANCE REQUIREMENTS

Precast Structural Concrete Units:  Comply with <<PCI MNL-116>>, <<PCI MNL-120>>, <<PCI MNL-123>>,  <<PCI MNL-135>>, <<ACI CODE-318>>,  <<ACI SPEC-301>>, <<ICC (IBC)>>, and applicable codes.

      - ***************************************************************************************

      - Retain this paragraph if Subcontractor is required to assume responsibility for design.

      - ***************************************************************************************

Delegated Design: Design precast structural concrete, including comprehensive engineering analysis by a qualified Professional Engineer, using performance requirements and design criteria indicated.

      - ***************************************************************************************

      - Retain "Fire-Resistance Calculations" Paragraph below if required for units or assemblies. If paragraph is retained then retain related Action Submittal Fire Resistance Calculations.

      - ***************************************************************************************

Fire-Resistance Calculations: Where indicated, provide precast structural concrete units whose fire resistance has been calculated according to <<PCI MNL-124>> and is acceptable to LANL Fire Protection.

Structural Performance: Precast structural concrete units and connections shall withstand design loads indicated on the drawings in accordance with the requirements of ​<< LANL TSM; or  LANL ESM>>​, within the limits and conditions indicated.

      - ***************************************************************************************

      - Retain paragraph above if design loads are shown on Drawings. Retain paragraph below if including design loads here. See the LANL ESM Chapter 5 - Structural  or LANL TSM Chapter 5 - Structural, as applicable, for required loads. Revise requirements below to suit Project, and add other performance and design criteria if applicable.

      - ***************************************************************************************

Structural Performance: Provide precast structural concrete units and connections capable of withstanding environmental design loads in accordance with the requirements of << LANL TSM; or  LANL ESM>>​​​ within the limits and conditions indicated below:

        - ******************************************************************************

        - For members that are to receive concrete topping, state whether all superimposed dead and live loads on precast, prestressed members do or do not include the weight of the concrete topping. It is best to list the live load, superimposed dead load, topping weight, and weight of the member, all as separate loads. Where there are two different live loads (e.g., roof level of a parking structure) indicate how they are to be combined. Show hanging utility support loads in addition to loads indicated on drawings.

        - ******************************************************************************

Risk Design Category: ​<< I;  II;  III; or  IV>>​.

Seismic Design Category: ​​<< D;  C; or  _______>>​​.

        - ******************************************************************************

        - Retain the applicable subparagraphs or the following from the following 7.

        - ******************************************************************************

Design loads as indicated in the drawings.

        - ***OR***

Superimposed Dead Loads: << ____>>.

Concrete Topping Load: ​​<< _______>>​​.

Live Loads: ​​<< _______>>​​.

Roof Loads: ​​​<< _______>>​​​

Self-Straining Thermal Loads: << _______>>

<< _______>>

        - ******************************************************************************

        - Retain the following subparagraph if required by the project. Show locations here or on Drawings if different movements are anticipated for different building elements.  Specify deflection limits stricter than ACI 318, if required.

        - ******************************************************************************

Design precast structural concrete framing system and connections to maintain clearances at openings, to allow for fabrication and construction tolerances, to accommodate live-load deflection, shrinkage and creep of primary building structure, and other building movements. Maintain precast structural concrete deflections within limits of <<ACI CODE-318>>.

          - **********************************************************************

          - Changes indicated below are based on temperature data from National Climatic Data Center, www.ncdc.noaa.gov, for Los Alamos: -18°F (Jan. ’63) and 102°F (Aug. ’44) are the min and max temperature extremes. Note that differential temperature movement is a function of the ambient temperature at the time of installation and the type of temperature controls in the building. AISC guidance for building design recommends checking most heated or air-conditioned steel buildings with a 50–70 °F design temperature range.

          - **********************************************************************

Thermal Movements: Allow for in-plane thermal movements resulting from annual ambient temperature changes of -18 to 102 degrees Fahrenheit.

        - ******************************************************************************

        - Retain subparagraph below if fire-resistance rating is required.  Fire ratings depend on occupancy and building construction type, and are generally a building code requirement. When required, fire-rated products should be clearly identified on the Drawings. In the subparagraph below “thickness” is with respect to concrete cover, for example, for cast-in place steel cables, reinforcing bars, structural elements, etc.

        - ******************************************************************************

Fire-Resistance Rating: Select material and minimum thicknesses to achieve fire rating << indicated on drawings.; and  as follows:>>

Roof Assembly:  ​<< ____>>​ hour.

Floor Assembly:  ​<< ____>>​ hour.

        - ******************************************************************************

        - Retain subparagraph below if precast units are used in parking structures to resist impact load.  Revise loads to suit Project.

        - ******************************************************************************

Vehicular Impact Loads: Design spandrel beams acting as vehicular barriers for passenger cars to resist a single ​​​<< 6000-lbf; or  _____-lbf>>​​​ load applied horizontally in any direction to the spandrel beam, with anchorages or attachments capable of transferring this load to the structure. Design spandrel beams assuming the load to act at a height of ​​​<< 18 or 27 inches>>​​​ above the floor or ramp surface, whichever is more severe, on an area not to exceed ​​​<< 1 square foot>>​​​.

MOLD MATERIALS

Molds:  Rigid, dimensionally stable, non-absorptive material, warp and buckle free, that will provide continuous and true precast concrete surfaces within fabrication tolerances indicated; nonreactive with concrete and suitable for producing required finishes.

Form-Release Agent: Commercially produced liquid-release agent that will not bond with, stain or adversely affect precast concrete surfaces and will not impair subsequent surface or joint treatments of precast concrete.

      - ***************************************************************************************

      - Retain paragraph below if using form liners for precast structural concrete with architectural finish.  Form liners may be used to achieve a special off-the-form finish.  Revise to add description of selected form liner if required.

      - ***************************************************************************************

Form Liners: Units of face design, texture, arrangement, and configuration << indicated; or  to match those used for precast concrete design reference sample>>. Furnish with manufacturer's recommended liquid-release agent that will not bond with, stain, or adversely affect precast concrete surfaces and will not impair subsequent surface or joint treatments of precast concrete.

      - ***************************************************************************************

      - Retain paragraph below if surface retarder is applied to molds to help obtain exposed-aggregate finish for precast structural concrete with architectural finish.

      - ***************************************************************************************

Surface Retarder:  Chemical set retarder, capable of temporarily delaying final hardening of newly placed concrete mixture to depth of reveal specified.

REINFORCING MATERIALS

All reinforcing steel must be traceable to manufacturer approved Certified Material Test Reports (CMTR’s).

      - ***************************************************************************************

      - Retain one or more of the following nine paragraphs in this article to suit steel reinforcement requirements. Distinguish locations of each type of reinforcement here or on Drawings. If retaining Article "Performance Requirements", consider reviewing selections with fabricators.

      - Retain "Recycled Content of Steel Products" Paragraph below if recycled content is required for LEED Credit MR 4.  USGBC allows a default value of 25 percent to be used for steel, without documentation; higher percentages can be claimed if they are supported by appropriate documentation.

      - ***************************************************************************************

Recycled Content of Steel Products: Postconsumer recycled content plus one-half of preconsumer recycled content not less than ​<< 25 percent;  60 percent; or  _______>>​.

      - ***************************************************************************************

      - Indicate reinforcing steel ASTM designation and grade in subparagraph in accordance with design requirements. ASTM A706 reinforcing steel is intended for applications where controlled tensile properties, or chemical composition restrictions to enhance weldability, or both, are required.

      - This distinction is highlighted by the fact that IBC and ACI 318 have restrictions pertaining to ASTM A615 reinforcing steel used to resist seismic forces and/or to be welded. These restrictions do not apply to ASTM A 706.

        - For the seismic requirements, reference ACI 318, 20.2.2.5(b)

        - For the welding requirements, reference IBC 1705.3 and ACI 318, 26.6.4

      - ***************************************************************************************

Reinforcing Bars: ​<< ASTM A615/A615M , Grade 60; or  ASTM A706/A706M>>​, deformed.

      - ***************************************************************************************

      - Retain galvanized reinforcing bars in paragraph below where corrosive environment or severe exposure conditions justify extra cost.  Presence of chromate film on the surface of galvanized coating is usually visible as light yellow tint on the surface.  ASTM B 201 describes a test method for determining presence of chromate coatings.

      - ***************************************************************************************

Galvanized Reinforcing Bars: ​​<< ASTM A615/A615M , Grade 60; or  ASTM A706/A706M>>​​, deformed bars, <<ASTM A767/A767M>>, Class II zinc coated, hot-dip galvanized​​<< , and chromate wash treated after fabrication and bending; or  None - N/A>>​​.

      - ***************************************************************************************

      - Consider using epoxy coating where corrosive environment or severe exposure conditions justify extra cost.  In paragraph below, retain ASTM A 775 for a bendable epoxy coating; retain ASTM A 934 for a nonbendable epoxy coating.

      - ***************************************************************************************

Epoxy-Coated Reinforcing Bars: ​​<< ASTM A615/A615M , Grade 60; or  ASTM A706/A706M>>​​, deformed bars, ​​<< ASTM A775/A775M; or  ASTM A924/A924M>>​​ epoxy coated, with less than 2 percent damaged coating in each 12-inch bar length.

Epoxy-Coated reinforcing steel must come from a plant certified by the Concrete Reinforcing Steel Institute, or the Engineer of Record must approve the facility.

Steel Bar Mats: <<ASTM A184/A184M>>, fabricated from ​<< ASTM A615/A615M , Grade 60; or  ASTM A706/A706M>>​, deformed bars, assembled with clips.

Plain-Steel Welded Wire Reinforcement: <<ASTM A1064/A1064M>>, fabricated from ​​<< as-drawn steel; or  galvanized steel>>​​ wire into flat sheets.

Deformed-Steel Welded Wire Reinforcement: <<ASTM A1064/A1064M>>, flat sheet.

Epoxy-Coated-Steel Wire: <<ASTM A884/A884M>>, Class A coated, ​<< plain; or  deformed>>​, flat sheet, ​<< Type 1 bendable; or  Type 2 non-bendable>>​ coating.

Supports: Suspend reinforcement from back of mold or use bolsters, chairs, spacers, and other devices for spacing, supporting, and fastening reinforcing bars and welded wire reinforcement in place according to <<PCI MNL-116>>.

      - ***************************************************************************************

      - Retain the following Article, along with applicable paragraphs and subparagraphs, as required by the project. Retain if precast concrete units will be prestressed, either pretensioned or post-tensioned.

      - ***************************************************************************************

PRESTRESSING TENDONS

      - ***************************************************************************************

      - Retain materials in this article as required; revise to suit Project.

      - Note that PCI MNL 120 states that there is limited use of two and three wire strands conforming to ASTM A910.

      - ***************************************************************************************

Prestressing Strand: << ASTM A416/A416M , Grade 250 or Grade 270, uncoated, 7-wire;  ASTM A882/A882M , Grade 270, 7-wire; or  ASTM A910/A910M , Grade 270, uncoated, weld-less, 2- and 3-wire>>, low-relaxation strand.

        - ******************************************************************************

        - For aggressive environments, revise subparagraph below by adding an anchorage device encapsulation system (from ACI 423.7) consisting of caps and sleeves.

        - ******************************************************************************

Coat unbonded post-tensioning strand with post-tensioning coating and sheath with polypropylene tendon sheathing. Include anchorage devices and coupler assemblies.

Post-Tensioning Bars: <<ASTM A722/A722M>>, uncoated high-strength steel bar.

CONCRETE MATERIALS

      - ***************************************************************************************

      - Retain materials in this article as required; revise to suit Project

      - Type III cement is not an option at LANL as a result of Jul 2012 input from NMDOT:

      - Pro:  Quick / short-term strength & stiffness gains (i.e., over those associated w/ Type I-II).

      - Con:  Less long-term strength & stiffness gains, & less durability (i.e., higher alkali content leads to greater potential for ASR; & higher temperature during curing leads to greater potential for shrinkage cracking, hence less freeze-thaw resistance).

      - In short, Type III cement sacrifices long-term performance for early-age strength & stiffness gains.

      - ***************************************************************************************

Portland Cement: <<ASTM C595/C595M>>​ or <<ASTM C150/C150M>>, Type I or Type II, gray, unless otherwise indicated.

        - ******************************************************************************

        - Retain subparagraph below if mixing white and gray cement will improve color uniformity of precast structural concrete with architectural finish.  White cement has greater color consistency than gray cement and can be used for pastel colors.  For darker colors, variations of gray cement have less effect on final color hue.

        - ******************************************************************************

For surfaces exposed to view in finished structure, mix gray with white cement, of same type, brand, and mill source.

Supplementary Cementitious Materials:

        - ******************************************************************************

        - Retain mineral or cementitious admixtures in four subparagraphs below.  Because fly ash, gray silica fume, and ground slag affect color uniformity, they are not recommended by PCI where appearance is important

        - ******************************************************************************

Fly Ash: <<ASTM C618>>, Class C or F, with maximum loss on ignition of 3 percent.

Metakaolin Admixture: <<ASTM C618>>, Class N.

Silica Fume Admixture: <<ASTM C1240>>, with optional chemical and physical requirement.

Ground Granulated Blast-Furnace Slag: <<ASTM C989/C989M>>, Grade 100 or 120.

      - ***************************************************************************************

      - ASTM C33 limits deleterious substances in coarse aggregate depending on climate severity and in-service location of concrete.  Class 5S is the most restrictive designation for architectural concrete exposed to severe weathering.  PCI MNL 116 also establishes strict limits on deleterious substances for fine and coarse aggregates

      - ***************************************************************************************

Normal-Weight Aggregates: Except as modified by <<PCI MNL-116>>, <<ASTM C33/C33M>>, with coarse aggregates complying with << Class 5S;  Class 5M;  Class 4S; or  Class 4M>>.  Stockpile fine and coarse aggregates for each type of exposed finish from a single source (pit or quarry) for Project.

        - ******************************************************************************

        - Retain the following subparagraphs if applicable.

        - ******************************************************************************

Face-Mixture-Coarse Aggregates: Selected, hard, and durable; free of material that reacts with cement or causes staining; to match selected finish sample.

          - **********************************************************************

          - Retain one option in subparagraph below or insert gradation and maximum aggregate size if known.  Fine and coarse aggregates are not always from same source.

          - **********************************************************************

Gradation:  << Uniformly graded;  Gap graded; or  To match design reference sample>>.

Face-Mixture-Fine Aggregates:  Selected, natural or manufactured sand of same material as coarse aggregate unless otherwise approved by EOR.

      - ***************************************************************************************

      - Lightweight aggregates in a face mixture are not recommended by PCI in cold or humid climates (if exposed to the weather) unless their performance has been verified by tests or records of previous satisfactory usage in similar environments.  If normal-weight aggregates are used in face mixture, PCI does not recommend lightweight aggregates in backup mixture due to bowing potential

      - ***************************************************************************************

Lightweight Aggregates:  Except as modified by <<PCI MNL-116>>, <<ASTM C330/C330M>>, with absorption less than 11 percent.

      - ***************************************************************************************

      - Retain paragraph below if coloring admixture is required for precast structural concrete with architectural finish.  Add color selection if known

      - ***************************************************************************************

Coloring Admixture:  <<ASTM C979/C979M>>, synthetic or natural mineral-oxide pigments or colored water-reducing admixtures, temperature stable, and nonfading.

Water:  Potable; free from deleterious material that may affect color stability, setting, or strength of concrete and complying with chemical limits of <<PCI MNL-116>>.

Air-Entraining Admixture:  <<ASTM C260/C260M>>, certified by manufacturer to be compatible with other required admixtures.

Chemical Admixtures:  Certified by manufacturer to be compatible with other admixtures and to not contain calcium chloride, or more than 0.15 percent chloride ions or other salts by weight of admixture.

        - ******************************************************************************

        - Retain one or more chemical admixtures in seven subparagraphs below if chemical admixtures are permitted; limit chemical admixture types if required.  Water-reducing admixtures, Types A, D, and E, or a high-range water reducer, Type F, predominate.

        - ******************************************************************************

Water-Reducing Admixtures: <<ASTM C494/C494M>>, Type A.

Retarding Admixture: <<ASTM C494/C494M>>, Type B.

Water-Reducing and Retarding Admixture: <<ASTM C494/C494M>>, Type D.

Water-Reducing and Accelerating Admixture: <<ASTM C494/C494M>>, Type E.

High-Range, Water-Reducing Admixture <<ASTM C494/C494M>>, Type F.

High-Range, Water-Reducing and Retarding Admixture:  <<ASTM C494/C494M>>, Type G.

Plasticizing and Retarding Admixture: <<ASTM C1017/C1017M>>.

      - ***************************************************************************************

      - Retain the following paragraph if required by the project.

      - ***************************************************************************************

Corrosion-Inhibiting Admixture:  Commercially formulated, anodic inhibitor or mixed cathodic and anodic inhibitor; capable of forming a protective barrier and minimizing chloride reactions with steel reinforcement in concrete.

STEEL CONNECTION MATERIALS

      - ***************************************************************************************

      - Revise this article to suit Project.  Add other materials as required.

      - ***************************************************************************************

Carbon-Steel Shapes and Plates: <<ASTM A36/A36M>>.

Carbon-Steel-Headed Studs: <<ASTM A108>>, AISI 1018 through AISI 1020, cold finished, <<AWS D1.1/D1.1M>>, Type A or B, with arc shields and with minimum mechanical properties of <<PCI MNL-116>>.

Carbon-Steel Plate: <<ASTM A283/A283M>>.

Malleable-Iron Castings: <<ASTM A47/A47M>>.

Carbon-Steel Castings: <<ASTM A27/A27M>>​, Grade 60-30.

High-Strength, Low-Alloy Structural Steel: <<ASTM A572/A572M>>.

Carbon-Steel Structural Tubing: <<ASTM A500/A500M>>, Grade B.

Wrought Carbon-Steel Bars: <<ASTM A675/A675M>>, Grade 65.

Deformed-Steel Wire or Bar Anchors: <<ASTM A1064/A1064M>> or <<ASTM A706/A706M>>.

      - ***************************************************************************************

      - ASTM A307 defines the term "studs" to include stud stock and threaded rods.

      - ***************************************************************************************

Carbon-Steel Bolts and Studs: <<ASTM A307>>, Grade A; carbon-steel, hex-head bolts and studs; carbon-steel nuts, <<ASTM A563/A563M>>; and flat, unhardened steel washers, <<ASTM F844>>.

      - ***************************************************************************************

      - High-strength bolts are used for friction-type connections between steel members and are not recommended by PCI between steel and concrete because concrete creep and crushing of concrete during bolt tightening reduce effectiveness.

      - ***************************************************************************************

High-Strength Bolts and Nuts: <<ASTM F3125/F3125M>>, Grade ​​​<< A325; or  A490>>​​​ ​​​<< Type 1; or  Type 2>>​​​, heavy hex steel structural bolts; heavy hex carbon-steel nuts, <<ASTM A563/A563M>>; and hardened carbon-steel washers, <<ASTM F436/F436M>>.

Do not zinc coat <<ASTM F3125/F3125M>> bolts.

      - ***************************************************************************************

      - Retain paragraph below if galvanized finish is required.  Revise locations of galvanized items if required.  Field welding is generally not permitted on galvanized elements unless galvanizing is removed or acceptable welding procedures are submitted.  Hot-dip galvanized finish provides greater corrosion resistance than electrodeposited zinc coating.  Electrodeposition is usually limited to threaded fasteners.

      - ***************************************************************************************

Zinc-Coated Finish: For exterior steel items​<< , steel in exterior walls,; or  None - N/A>>​ and items indicated for galvanizing, apply zinc coating by ​<< hot-dip process according to ASTM A123/A123M or ASTM A153/A153M; or  electrodeposition according to  ASTM B633 , SC 3, Types 1 and 2>>​.

For steel shapes, plates, and tubing to be galvanized, limit silicon content of steel to less than 0.03 percent or to between 0.15 and 0.25 percent or limit sum of silicon and 2.5 times phosphorous content to 0.09 percent.

Galvanizing Repair Paint: High-zinc-dust-content paint with dry film containing not less than 94 percent zinc dust by weight, and complying with <<MIL-P-21035B>> or <<SSPC-Paint 20>>.

      - ***************************************************************************************

      - Retain paragraph below if paint finish is required.  Revise locations of priming if required.  MPI 79 in first option provides some corrosion protection, while SSPC-Paint 25, without topcoating, provides minimal corrosion protection

      - ***************************************************************************************

Shop-Primed Finish: Prepare surfaces of non-galvanized-steel items, except those surfaces to be embedded in concrete, according to requirements in <<SSPC-SP 3>>​, and shop apply lead- and chromate-free, rust-inhibitive primer, complying with performance requirements in <<MPI #79>> according to <<SSPC-PA 1>>.

Welding Electrodes: Comply with AWS standards.

Precast Accessories: Provide clips, hangers, plastic or steel shims, and other accessories required to install precast structural concrete units.

​<< insert additional materials>>​.

      - ***************************************************************************************

      - Retain this article when resistance to staining merits extra cost in parking structures and other high-moisture or corrosive areas

      - ***************************************************************************************

STAINLESS STEEL CONNECTION MATERIALS

Stainless Steel Plate: <<ASTM A666/A666M>>, Type 304, of grade suitable for application.

Stainless Steel Bolts and Studs: <<ASTM F593>>, Alloy 304 or 316, hex-head bolts and studs; stainless-steel nuts; and flat, stainless-steel washers. Lubricate threaded parts of stainless-steel bolts with an antiseize thread lubricant during assembly.

Stainless Steel Headed Studs: <<ASTM A276/A276M>>, with minimum mechanical properties of <<PCI MNL-116>>.

      - ***************************************************************************************

      - Retain this article if applicable.  Coordinate selection of bearing pad with fabricator.

      - ***************************************************************************************

BEARING PADS

Provide one of the following bearing pads for precast structural concrete units​​<< as recommended by precast fabricator for application; or  None - N/A>>​​:

        - ******************************************************************************

        - Retain the applicable subparagraphs from the following.

        - ******************************************************************************

Elastomeric Pads: <<AASHTO M 251M/M 251>>, plain, vulcanized, 100 percent polychloroprene (neoprene) elastomer, molded to size or cut from a molded sheet, 50 to 70 Shore, Type A durometer hardness, <<ASTM D2240>>; minimum tensile strength 2,250 psi, <<ASTM D412>>.

Random-Oriented, Fiber-Reinforced Elastomeric Pads: Preformed, randomly oriented synthetic fibers set in elastomer. 70 to 90 Shore, Type A durometer hardness, <<ASTM D2240>>; capable of supporting a compressive stress of 3,000 psi with no cracking, splitting, or delaminating in the internal portions of pad. Test 1 specimen for every 200 pads used in Project.

Cotton-Duck-Fabric-Reinforced Elastomeric Pads: Preformed, horizontally layered cotton-duck fabric bonded to an elastomer; 80 to 100 Shore, Type A durometer hardness, <<ASTM D2240>>; complying with “Elastomeric Pads and Steel-Reinforced Elastomeric Bearings— Method A" in <<AASHTO LRFDCONS>>, or with <<MIL-DTL-882F>>.

Frictionless Pads:  Tetrafluoroethylene, glass-fiber reinforced, bonded to stainless- or mild-steel plate, of type required for in-service stress.

High-Density Plastic:  Multimonomer, nonleaching, plastic strip.

GROUT MATERIALS

      - ***************************************************************************************

      - If grout is to be used in post-tensioned concrete for bonded tendons then add a paragraph herein that is in accordance with guidance provided in PTI M55.1, “Specification for Grouting of Post-Tensioned Structures.”  This paragraph shall indicate that the water-soluble chloride ion content of the grout shall be < 0.06 per ACI 318.

      - Add other proprietary grout systems to suit Project.  Show locations of each grout in this article or on Drawings if retaining more than one type.  Sand-cement grout in first paragraph below is commonly used in keyed joints between hollow-core floor and roof slabs and wall units.

      - ***************************************************************************************

Sand-Cement Grout: Portland cement, <<ASTM C150/C150M>>, Type I, and clean, natural sand, <<ASTM C144>> or <<ASTM C404>>. Mix at ratio of 1 part cement to 2-1/2 parts sand, by volume, with minimum water required for placement and hydration.

      - ***************************************************************************************

      - Retain paragraph below if nonshrink grout is required, or if cement-grout shrinkage could cause structural deficiency.  For critical installations, require manufacturer to provide field supervision.

      - ***************************************************************************************

Nonmetallic, Nonshrink Grout: Premixed, nonmetallic, noncorrosive, nonstaining grout containing selected silica sands, Portland cement, shrinkage-compensating agents, plasticizing and water-reducing agents, complying with <<ASTM C1107/C1107M>>, Grade A for drypack and Grades B and C for flowable grout and of consistency suitable for application within a 30-minute working time.

      - ***************************************************************************************

      - Retain the following paragraph if required by the project.

      - ***************************************************************************************

Epoxy-Resin Grout: Two-component, mineral-filled epoxy resin; <<ASTM C881/C881M>>, of type, grade, and class to suit requirements.

      - ***************************************************************************************

      - If the project includes post-tensioned concrete with bonded tendons, the following article shall be added to address requirements for tendon ducts. Guidance for this article is provided in PTI M50.3, Guide Specification for Grouted Post-Tensioning, and PTI M55.1.

      - ***************************************************************************************

DUCTS

<< _______>>

      - ***************************************************************************************

      - Retain this article if Reveals are required.

      - ***************************************************************************************

Reveal and Accent Strips

      - ***************************************************************************************

      - Retain the following paragraph if required by the project.

      - Edit the subsequent descriptive specifications to identify project requirements and to eliminate any conflict with specified manufacturer's products.

      - The manufacturers listed are representative of those offering the products of this section. Verify each manufacturer's ability to provide product(s) specified for each project.

      - ***************************************************************************************

Manufacturers:

Nox-Crete Inc; Clean Line Reveal.

​<< ______>>​.

​<< ______>>​.

Material: Non-staining, non-reactive​<< , high-density polyethylene;  , _______; or  None - N/A>>​.

      - ***************************************************************************************

      - Select one of the following two paragraphs.

      - ***************************************************************************************

Profile(s): As selected by EOR from manufacturer's standard range.

      - *** OR ***

Profile(s):  ​<< As indicated on drawings;  As indicated; or  _______>>​.

      - ***************************************************************************************

      - Retain this article if insulated flat-wall panels are required.

      - ***************************************************************************************

INSULATED FLAT-WALL PANEL ACCESSORIES

      - ***************************************************************************************

      - Retain insulation material in one of first three paragraphs below; if using more then one type, identify location of each on Drawings

      - ***************************************************************************************

Molded-Polystyrene Board Insulation: <<ASTM C578>>, ​<< Type I, 0.90 lb/cu.ft.;  Type VIII,  1.15 lb/cu.ft.; or  Type II,  1.35 lb/cu.ft.>>​; ​<< square; or  ship-lap>>​ edges; with R-value of ​<< _______>>​ and thickness of ​<< _______>>​.

Extruded-Polystyrene Board Insulation: ASTM C <<ASTM C578>>, ​<< Type IV, 1.60 lb/cu.ft.;  Type X,  1.30 lb/cu.ft.; or  Type VI,  1.80 lb/cu.ft.>>​; ​<< square; or  ship-lap>>​ edges; with R-value of ​<< _______>>​  and thickness of ​<< _______>>​​.

Polyisocyanurate Board Insulation: <<ASTM C591>>, << Type I, 1.8 lb/cu.ft.;  Type IV,  2.0 lb/cu.ft.; or  Type II,  2.5 lb/cu.ft.>> unfaced, with R-value of << _______>> and thickness of << _______>>.

      - ***************************************************************************************

      - Retain one or more wythe connectors in paragraph below.

      - ***************************************************************************************

Wythe Connectors: ​<< Glass-fiber connectors;  Vinyl-ester polymer connectors;  Polypropylene pin connectors;  Stainless-steel pin connectors;  Bent galvanized reinforcing bars;  Galvanized welded wire trusses;  Galvanized bent wire connectors; and  Cylindrical metal sleeve anchors>>​ manufactured to connect wythes of precast concrete panels.

CONCRETE MIXTURES

Prepare design mixtures for each type of precast concrete required.

        - ******************************************************************************

        - Alkali-Silica Reactivity: The mix design for LANL precast concrete shall contain from 20% to 30% by weight of total cementitious material Type F fly ash conforming to ASTM C 618 for mitigating the deleterious effects of alkali-silica reaction in concrete that is common with the siliceous nature of aggregates found in northern New Mexico. This requirement allows precast concrete from local fabricators to be used. Alkali silica reaction is the reaction between the alkali hydroxide in Portland cement and certain siliceous rocks and minerals present in the aggregates, such as opal, chert, chalcedony, trydymite, cristobalite, strained quartz, etc. The products of this reaction often result in significant expansion and cracking of the concrete, and ultimately failure of the concrete structure, including significant potential for foreign object damage.

        - The Engineer of Record may specify a mix design that does not utilize fly ash or other ASR inhibiting admixtures only if the precast plant can produce certified suppliers test reports that show the aggregate is nonreactive according to a preapproved testing standard and durability tests of long term performance show no deleterious effects. This may be the case for out of state precast manufacturers that use aggregate sources in which reactivity is not a concern.

        - ******************************************************************************

All design mixtures must have a minimum of 20 percent fly ash or pozzolan to assure against alkali-resistivity.

        - ******************************************************************************

        - Retain subparagraph below if required for LEED-NC, LEED-CS, or LEED for schools Credit ID 1. This credit can be achieved by replacing at least 40 percent of the Portland cement, which would otherwise be used in concrete, with other cementitious materials.  40 percent replacement value applies to the average of all concrete used for Project; requirement below can be reduced if requirement for other concrete on Project is increased sufficiently to make up for the reduction

        - ******************************************************************************

Use fly ash, pozzolan, ground granulated blast-furnace slag, and silica fume as needed to reduce the total amount of Portland cement, which would otherwise be used, by not less than 40 percent.

        - ******************************************************************************

        - Retain subparagraph below if fly ash, granulated blast-furnace slag, or metakaolin and silica fume are permitted. Percentages are PCI examples; revise to suit Project.

        - ******************************************************************************

Limit use of fly ash to 30 percent replacement of Portland cement by weight and granulated blast-furnace slag to 40 percent of Portland cement by weight; metakaolin and silica fume to 10 percent of Portland cement by weight.

Design mixtures may be prepared by a qualified independent testing agency or by qualified precast plant personnel at precast structural concrete fabricator's option.

Design mixtures must be approved by the Engineer of Record and LANL Structural SME (LANL may consider whether approved by NMDOT State Materials Bureau for NMDOT Standard Specifications).

Limit water-soluble chloride ions to maximum percentage by weight of cement permitted by  <<ACI CODE-318>> or <<PCI MNL-116>> when tested according to <<ASTM C1218/C1218M>>.

      - ***************************************************************************************

      - Precast structural concrete with architectural finish may be manufactured with a separate face mixture and a structural backup mixture. Face and backup mixtures require similar shrinkage and expansion coefficients. Similar water-cementitious materials ratios and cement-aggregate ratios are recommended by PCI to limit bowing or warping.

      - Retain first option in first paragraph below if lightweight backup concrete mix is required; second option if normal-weight face and backup mixtures are required; third option if full-depth, normal-weight mixture is required; or fourth option if choice of normal-weight face and backup mixtures or full-depth mixtures is fabricator's option.

      - ***************************************************************************************

Normal-Weight Concrete Mixtures: Proportion << face mixtures;  face and backup mixtures;  full-depth mixture; or  face and backup mixtures or full-depth mixture, at fabricator's option,>> by either laboratory trial batch or field test data methods according to <<ACI PRC-211.1>>, with materials to be used on Project, to provide normal-weight concrete with the following properties:

        - ******************************************************************************

        - Revise the following subparagraph below. Higher-strength mixtures may be available; verify availability with fabricators.

        - ******************************************************************************

Compressive Strength (28 Days): << 5000 psi>> .

        - ******************************************************************************

        - Water-cementitious materials ratio of 0.40 to 0.45 is usual for precast structural concrete. Lower ratios may be possible with use of high-range water reducers. Revise ratio in subparagraph below to suit Project.

        - ******************************************************************************

Maximum Water-Cementitious Materials Ratio: << 0.45>>​.

      - ***************************************************************************************

      - Water absorption indicates susceptibility to weather staining. PCI states that limits in paragraph below are suitable for average exposures. Different parts of a single panel cannot be produced with different absorptions. Verify that fabricators can produce units with lower water absorption because special consolidation techniques to increase concrete density are required.

      - ***************************************************************************************

Water Absorption: 6 percent by weight or 14 percent by volume, tested according to <<PCI MNL-116>>.

      - ***************************************************************************************

      - To minimize bowing or warping, PCI does not recommend lightweight backup mixtures with normal-weight face mixtures. Retain the following paragraph  if required or as an option if satisfactory durability and in-service performance are verified by fabricator. Coordinate with selection of normal-weight face mixture option above.

      - ***************************************************************************************

Lightweight Concrete Backup Mixtures: Proportion mixtures by either laboratory trial batch or field test data methods according to <<ACI PRC-213>>, with materials to be used on Project, to provide lightweight concrete with the following properties:

        - ******************************************************************************

        - Revise the following subparagraph below to suit Project. Higher-strength mixtures may be available; verify availability with fabricators.

        - ******************************************************************************

Compressive Strength (28 Days): << 5000 psi>>.

        - ******************************************************************************

        - Increase or decrease unit weight in subparagraph below to suit Project. Coordinate with lightweight-aggregate supplier and precast structural concrete fabricator. Lightweight concretes with lightweight and normal-weight aggregate in mixture will usually be heavier than unit weight below.

        - ******************************************************************************

Unit Weight: Calculated equilibrium unit weight of ​​<< 115 lb/cu.ft.>>​​, plus or minus ​​<< 3 lb/cu.ft.>>​​, according to <<ASTM C567/C567M>>.

Add air-entraining admixture at manufacturer's prescribed rate to result in concrete at point of placement having an air content complying with <<PCI MNL-116>>.

When included in design mixtures, add other admixtures to concrete mixtures according to manufacturer's written instructions.

Concrete Mix Adjustments: Concrete mix design adjustments may be proposed if characteristics of materials, Project conditions, weather, test results, or other circumstances warrant.

      - ***************************************************************************************

      - ACI 318, Ch. 19, Durability, requires the EOR to “…assign exposure classes in accordance with the severity of the anticipated exposure of structural concrete members for each exposure category according to Table 19.3.1.1.” The typical exposure category (in Table 19.3.1.1) of concern at LANL is F, Freezing and Thawing, and the typical upper-bound severity of exposure is Severe, F2.

      - The EOR will specify the concrete exposure category and class in the design.

      - The Engineer of Record will specify if durability testing of the concrete mix is required.

      - ***************************************************************************************

Durability: Ensure concrete mixture complies with <<ACI CODE-318>> Chapter 19 and <<PCI MNL-116>> for durability.

      - ***************************************************************************************

      - Retain the following paragraph if required by the project.

      - ***************************************************************************************

Durability Testing: ​​​<< Not required; or  Tested in accordance with ASTM C666/C666M and other applicable standards>>​​​.

MOLD FABRICATION

Molds:  Accurately construct molds, mortar tight, of sufficient strength to withstand pressures due to concrete-placement operations and temperature changes and for prestressing and detensioning operations.  Coat contact surfaces of molds with release agent before reinforcement is placed.  Avoid contamination of reinforcement and prestressing tendons by release agent.

        - ******************************************************************************

        - Retain form liners in subparagraph below if needed to produce exposed surface finish on precast structural concrete with architectural finish.

        - ******************************************************************************

Place form liners accurately to provide finished surface texture indicated.  Provide solid backing and supports to maintain stability of liners during concrete placement.  Coat form liner with form-release agent.

Maintain molds to provide completed precast structural concrete units of shapes, lines, and dimensions indicated, within fabrication tolerances specified.

        - ******************************************************************************

        - Retain first subparagraph below for precast structural concrete with architectural finishes.

        - ******************************************************************************

Form joints are not permitted on faces exposed to view in the finished work.

        - ******************************************************************************

        - Retain one option from subparagraph below; show details on Drawings or revise description to add dimensions. Sharp edges or corners of precast concrete units are vulnerable to chipping.

        - ******************************************************************************

Edge and Corner Treatment: Uniformly ​<< chamfered; or  radiused>>​.

FABRICATION

Cast-in Anchors, Inserts, Plates, Angles, and Other Anchorage Hardware:  Fabricate anchorage hardware with sufficient anchorage and embedment to comply with design requirements.  Accurately position for attachment of loose hardware, and secure in place during precasting operations.  Locate anchorage hardware where it does not affect position of main reinforcement or concrete placement.

Weld-headed studs and deformed bar anchors used for anchorage according to Section << 01 4455 - Onsite Welding, Brazing and Joining Requirements>>, and <<AWS D1.1/D1.1M>> and <<AWS C5.4>>​

Temporary anchors in precast structural concrete units shall be cast-in anchors and shall comply with all of the provisions associated with them.

      - ***************************************************************************************

      - Coordinate paragraph below with Section << 05 5000 - Metal Fabrications>> for furnishing and installing loose hardware items.

      - ***************************************************************************************

Furnish loose hardware items including steel plates, clip angles, seat angles, anchors, dowels, cramps, hangers, and other hardware shapes for securing precast structural concrete units to supporting and adjacent construction.

Cast-in reglets, slots, holes, and other accessories in precast structural concrete units as indicated on the Subcontract Drawings.

      - ***************************************************************************************

      - Retain paragraph below if applicable.

      - ***************************************************************************************

Cast-in openings larger than 10 inches in any dimension.  Do not drill or cut openings or prestressing strand without EOR's approval.

Reinforcement: Comply with recommendations in <<PCI MNL-116>> for fabricating, placing, and supporting reinforcement.

Clean reinforcement of loose rust and mill scale, earth, and other materials that reduce or destroy the bond with concrete.  When damage to epoxy-coated reinforcement exceeds limits specified, repair with patching material compatible with coating material and epoxy coat bar ends after cutting.

Accurately position, support, and secure reinforcement against displacement during concrete-placement and consolidation operations.  Completely conceal support devices to prevent exposure on finished surfaces.

Place reinforcing steel and prestressing strand to maintain at least 3/4-inch minimum concrete cover.  Increase cover requirements for reinforcing steel to 1-1/2 inches when units are exposed to corrosive environment or severe exposure conditions.  Arrange, space, and securely tie bars and bar supports to hold reinforcement in position while placing concrete.  Direct wire tie ends away from finished, exposed concrete surfaces.

Install welded wire fabric in lengths as long as practicable.  Lap adjoining pieces at least one, full mesh-spacing, and wire tie laps where required by design.  Offset laps of adjoining widths to prevent continuous laps in either direction.

Reinforce precast structural concrete units to resist handling, transportation, and erection stresses.

      - ***************************************************************************************

      - Retain paragraph below if precast, prestressed structural concrete units are required. Decision to prestress may be left to fabricator if objective is to aid handling and to control cracking of units during installation.

      - ***************************************************************************************

Prestress tendons for precast structural concrete units by either pretensioning or post-tensioning methods. Comply with <<PCI MNL-116>>​<< and  PTI TAB.1 -06; or  None - N/A>>​.

        - ******************************************************************************

        - In accordance with IBC paragraph 1901.4 and ACI 318 paragraph 26.4.2.1(c), the minimum concrete compressive strength at the time of transfer/release of the prestressing force shall be indicated on the drawings, in the first subparagraph below, or both.

        - For information on the subject of, and the requirements associated with, ‘transfer/release’ and associated ‘compressive strength’ refer to the following:

        - Pre-tensioning (i.e., detensioning and minimum concrete transfer strength): ACI 318 paragraphs 24.5 and 25.4.8, PCI MNL-120 paragraphs 5.2.2 and 5.2.3, and PCI MNL-116 paragraphs 4.1.2 and 5.3.17.

        - Post-tensioning (i.e., tensioning and minimum concrete transfer strength/ concrete strength at jacking): ACI 318 paragraphs 24.5 and 25.9, and PCI MNL-116 paragraphs 4.1.2 and 5.4.4.

        - ******************************************************************************

Do not detension pre-tensioning tendons, or tension post-tensioning tendons, of precast, prestressed structural concrete units until concrete has achieved ​<< ______>>​​<< the associated indicated; or  None - N/A>>​ compressive strength as established by test cylinders cured under same conditions as concrete.

        - ******************************************************************************

        - The following 12 subparagraphs are a designer-choice.

        - ******************************************************************************

Detension pretensioned tendons either by gradually releasing tensioning jacks or by heat cutting tendons, using a sequence and pattern to prevent shock or unbalanced loading.

If concrete has been heat cured, detension while concrete is still warm and moist to avoid dimensional changes that may cause cracking or undesirable stresses.

Perform post-tensioning in steps and measure the prestressing force, elongation of tendons, and indicate actual location of tendons. Maintain jacking and tensioning records for Project Records Submittals.

Jack against tendon pressure plate.

Prestressing force and friction losses shall be verified by a. and b.

Measured elongation of prestressed reinforcement compared with elongation calculated using the modulus of elasticity determined from tests or as reported by the manufacturer.

Jacking force measured using calibrated equipment such as a hydraulic pressure gauge, load cell, or dynamometer.

The cause of any difference in force determination between a. and b. above that exceeds 5 percent for pretensioned construction or 7 percent for post-tensioned construction shall be ascertained and corrected, unless otherwise approved by the EOR.

Loss of prestress force due to unreplaced broken prestressed reinforcement shall not exceed 2 percent of the total prestress force in prestressed concrete members.

If the transfer of force from the anchorages of the pretensioning bed to the concrete is accomplished by flame cutting prestressed reinforcement, the cutting locations and cutting sequence shall be selected to avoid undesired temporary stresses in pretensioned members.

Long lengths of exposed pretensioned strand shall be cut near the member to minimize shock to the concrete.

Prestressing reinforcement in post-tensioned construction shall not be stressed until the concrete compressive strength is at least ​<< 2500 psi>>​ for single-strand or bar tendons, ​<< 4000 psi>>​ for multistrand tendons, or a higher strength, if required.​<< An exception to these strength requirements is provided in the following subparagraph.; or  None - N/A>>​

Lower concrete compressive strength than required by the previous paragraph shall be permitted if either of the subparagraphs below are satisfied:

Oversized anchorage devices are used to compensate for a lower concrete compressive strength.

Prestressing reinforcement is stressed to no more than 50 percent of the final prestressing force.

        - ******************************************************************************

        - Note that for bonded tendons the Post-Tensioning Manual PTI TAB.1-06 gives a very thorough discussion regarding grouting when bonded tendons are used, including equipment and construction procedures. PTI M55.1, Specification for Grouting of Post-Tensioned Structures, is also a good resource.

        - ******************************************************************************

Bonded tendons: Inject grout continuously, in one direction, and in one stage.

Protect tendons, couplers, end fittings, post-tensioning anchorages and anchorage regions with bituminous, zinc-rich, or epoxy paint to avoid corrosion and possible rust spots. If/ when conditions do not allow for the paint described to either be applied or be effective, use of concrete cover or cement grout in metal or plastic duct are permissible.

        - ******************************************************************************

        - Retain subparagraph below only when appearance of member ends is critical or when exposed to severe environment.

        - ******************************************************************************

Protect strand ends and anchorages with a minimum of 1-inch-thick, nonmetallic, nonshrink, grout mortar and sack rub surface.  Coat or spray the inside surfaces of pocket with bonding agent before installing grout.

If approved by the EOR, items embedded while the concrete is in a plastic state shall satisfy 1 through 4:

Embedded items shall protrude from the precast concrete members or remain exposed for inspection.

Embedded items are not required to be hooked or tied to reinforcement within the concrete.

Embedded items shall be maintained in the correct position while the concrete remains plastic.

The concrete shall be consolidated around embedded items.

Comply with requirements in <<PCI MNL-116>> and in this Section for measuring, mixing, transporting, and placing concrete. After concrete batching, no additional water may be added.

      - ***************************************************************************************

      - Retain paragraph below if a separate face mixture is proposed for precast structural concrete with architectural finish.

      - ***************************************************************************************

Place face mixture to a minimum thickness after consolidation of the greater of << 1 inch>> or 1.5 times the maximum aggregate size, but not less than the minimum reinforcing cover specified.

Place concrete in a continuous operation to prevent seams or planes of weakness from forming in precast concrete units.

        - ******************************************************************************

        - Retain subparagraph below if a separate face mixture is proposed for precast structural concrete with architectural finish.

        - ******************************************************************************

Place backup concrete mixture to ensure bond with face-mixture concrete.

Thoroughly consolidate placed concrete by internal and external vibration without dislocating or damaging reinforcement and built-in items, and minimize pour lines, honeycombing, or entrapped air on surfaces. Use equipment and procedures complying with <<PCI MNL-116>>.

        - ******************************************************************************

        - Retain subparagraph below if permitting self-consolidating concrete.

        - ******************************************************************************

Place self-consolidating concrete without vibration according to <<PCI TR-6>>.

Comply with <<ACI 306.1>> procedures for cold-weather concrete placement.

Comply with <<PCI MNL-116>> procedures for hot-weather concrete placement.

Identify pickup points of precast structural concrete units and orientation in structure with permanent markings, complying with markings indicated on Shop Drawings.  Imprint or permanently mark casting date on each precast structural concrete unit on a surface that will not show in finished structure.

Cure concrete, according to requirements in <<PCI MNL-116>>, by moisture retention without heat or by accelerated heat curing* using low-pressure live steam or radiant heat and moisture. Cure units until compressive strength is high enough to ensure that stripping does not have an effect on performance or appearance of final product.

      - ________________________

      - *If accelerated curing is used (1) the compressive strength at the load stage considered shall be greater than the strength required at that load stage, and (2) It shall not impair the durability of the concrete.

Discard and replace precast structural concrete units that do not comply with requirements, including structural, manufacturing tolerance, and appearance, unless repairs meet requirements in <<PCI MNL-116>> and meet EOR's approval.

      - ***************************************************************************************

      - Retain this article if integrally insulated wall panels are required.

      - ***************************************************************************************

CASTING INSULATED WALL PANELS

Cast and screed wythe supported by mold.

Place insulation boards abutting edges and ends of adjacent boards.  Insert wythe connectors through insulation, and consolidate concrete around connectors according to connector manufacturer's written instructions.

Ensure bottom wythe and insulation layer are not disturbed after bottom wythe reaches initial set.

Cast and screed top wythe to meet required finish.

FABRICATION TOLERANCES

Fabricate precast structural concrete units straight and true to size and shape with exposed edges and corners precise and true so each finished unit complies with <<ACI ITG-7>> member dimension tolerances.​​<<  Tolerances for placement of prestressing tendons and post-tensioning ducts shall also comply with ACI ITG-7 .; or  None - N/A>>​​

COMMERCIAL FINISHES

      - ***************************************************************************************

      - Retain type of commercial structural finish, grouped by PCI as a "C" designation, in one or more of first four paragraphs below. If more than one finish is required, create a finish schedule, add locations to finish descriptions, or indicate on Drawings. Finishes below are in ascending order of finish quality and cost. Insert other specific finish requirements to suit Project.

      - Retain "Commercial Grade" Paragraph below when product will not be visible in completed structure or when function of structure does not require an enhanced surface. This finish is essentially an "as-cast" one.

      - ***************************************************************************************

Commercial Grade: Remove fins and large protrusions and fill large holes. Rub or grind ragged edges. Faces must have true, well-defined surfaces. Air holes, water marks, and color variations are permitted. Limit form joint offsets to << 3/16 inch>>.

      - ***************************************************************************************

      - Retain "Standard Grade" Paragraph below where products are exposed to view but function of structure does not require a special finish. Surface is suitable for an applied textured coating but not necessarily suitable for painting. This finish is typical for structural products.

      - ***************************************************************************************

Standard Grade: Normal plant-run finish produced in molds that impart a smooth finish to concrete. Surface holes smaller than << 1/2 inch>> caused by air bubbles, normal color variations, form joint marks, and minor chips and spalls are permitted. Fill air holes greater than << 1/4 inch>> in width that occur more than once per << 2 sq.in.>>. Major or unsightly imperfections, honeycombs, or structural defects are not permitted. Limit joint offsets to << 1/8 inch>>.

      - ***************************************************************************************

      - Retain "Grade B Finish" Paragraph below for visually exposed structural members such as columns or walls.

      - ***************************************************************************************

Grade B Finish: Fill air pockets and holes larger than << 1/4 inch>> in diameter with sand-cement paste matching color of adjacent surfaces. Fill air holes greater than << 1/8 inch>> in width that occur more than once per << 2 sq.in.>>. Grind smooth form offsets or fins larger than << 1/8 inch>>. Repair surface blemishes due to holes or dents in molds. Discoloration at form joints is permitted.

      - ***************************************************************************************

      - Retain "Grade A Finish" Paragraph below where surface will be painted or coated with a textured or sanded coating; some surface blemishes will be visible. If a surface with fewer imperfections than permitted Grade A finish is needed, retain a finish from Article "Commercial Architectural Finishes". Grade A finish is not applicable to extruded precast structural concrete products using zero-slump concrete in their process.

      - ***************************************************************************************

Grade A Finish: Fill surface blemishes with the exception of air holes << 1/16 inch>> in width or smaller, and form marks where the surface deviation is less than << 1/16 inch>>. Float apply a neat cement-paste coating to exposed surfaces. Rub dried paste coat with burlap to remove loose particles. Discoloration at form joints is permitted. Grind smooth all form joints.

      - ***************************************************************************************

      - Retain one of the following two paragraphs below. Screed or float finish in first paragraph is standard with PCI for unformed surfaces. Revise to describe extent to which float or trowel marks, variations of texture, or other surface blemishes will be permitted. Require samples to establish acceptance criteria for any exposed finish. Revise finish below to light-broom or as-cast finish if float finish is unnecessary.

      - ***************************************************************************************

Screed or float finish unformed surfaces. Strike off and consolidate concrete with vibrating screeds to a uniform finish. Hand screed at projections.  Normal color variations, minor indentations, minor chips, and spalls are permitted. Major imperfections, honeycombing, or defects are not permitted.

      - ***************************************************************************************

      - Retain first paragraph below if upgrading unformed surfaces to smooth, steel trowel finish.

      - ***************************************************************************************

Smooth, steel trowel finish unformed surfaces. Consolidate concrete, bring to proper level with straightedge, float, and trowel to a smooth, uniform finish.

      - ***************************************************************************************

      - Retain paragraph below if composite concrete topping is required to act structurally with precast floor or roof.

      - ***************************************************************************************

Apply roughening to a full amplitude of approximately << 1/4 inch>> to precast concrete floor or roof units that will receive concrete topping after installation.

      - ***************************************************************************************

      - Retain this article if precast structural concrete receives an architectural finish. Indicate on Drawings which members require architectural finish.

      - ***************************************************************************************

COMMERCIAL ARCHITECTURAL FINISHES

Manufacture member faces free of joint marks, grain, and other obvious defects with corners, including false joints, uniform, straight, and sharp. Finish exposed-face surfaces of precast concrete units to match approved ​​<< sample panels;  mockups; or  design reference sample>>​ and as follows:

        - ******************************************************************************

        - Retain subparagraph below if EOR has preapproved one or more design reference samples. Include complete description of design reference sample here. If preapproving fabricators, coordinate with Article "Manufacturers". Revise if multiple samples are approved.

        - ******************************************************************************

Design Reference Sample: << Insert description and identify fabricator and code number of sample>>.

        - ******************************************************************************

        - Retain subparagraph below if required. If retaining, revise and add reference number; PCI publishes numbered, color photographs of hundreds of precast concrete finishes; see PCI's Web site, www.pci.org. Add reference number combinations if more than one finish is required.

        - ******************************************************************************

PCI's Architectural Precast Concrete - Color and Texture Selection Guide, of plate numbers indicated.

        - ******************************************************************************

        - Select type of finish from nine subparagraphs below if needed. If more than one finish is required, create a finish schedule, add locations to finish descriptions, or indicate on Drawings. Add more-detailed descriptions of finishes outlined below if greater definition, such as light, medium, or deep reveal to finishes that expose the aggregate, is required. See PCI MNL 117 for more information on architectural finishes.

        - Retain first subparagraph below if a smooth-surface finish, an as-cast finish, which generally results in a mottled surface or non-uniform finish, is required.

        - ******************************************************************************

Smooth-Surface Finish: Provide surfaces free of excessive air voids, sand streaks, and honeycombs, with uniform color and texture.

Textured-Surface Finish: Impart by form liners or inserts to provide surfaces free of pockets, streaks, and honeycombs, with uniform color and texture.

Bushhammer Finish: Use power or hand tools to remove matrix and fracture coarse aggregates.

Exposed-Aggregate Finish: Use chemical-retarding agents applied to concrete molds and washing and brushing procedures to expose aggregate and surrounding matrix surfaces after form removal.

Abrasive-Blast Finish: Use abrasive grit, equipment, application techniques, and cleaning procedures to expose aggregate and surrounding matrix surfaces.

Acid-Etched Finish: Use acid and hot-water solution, equipment, application techniques, and cleaning procedures to expose aggregate and surrounding matrix surfaces. Protect hardware, connections, and insulation from acid attack.

Honed Finish: Use continuous mechanical abrasion with fine grit, followed by filling and rubbing procedures.

Polished Finish: Use continuous mechanical abrasion with fine grit, followed by filling and rubbing procedures.

Sand-Embedment Finish: Use selected stones placed in a sand bed in bottom of mold, with sand removed after curing.

SOURCE QUALITY CONTROL

      - ***************************************************************************************

      - Always retain first paragraph below because it establishes a minimum standard of plant testing and inspecting. PCI MNL 116 mandates source testing requirements and a plant "Quality Systems Manual." PCI plant certification also ensures periodic auditing of plants complying with PCI MNL 116.

      - ***************************************************************************************

Quality-Control Testing: Test and inspect precast structural concrete according to <<PCI MNL-116>> requirements.

        - ******************************************************************************

        - Retain subparagraph below if permitting self-consolidating concrete.

        - ******************************************************************************

Test and inspect self-consolidating concrete according to <<PCI TR-6>>.

Special Inspections: In addition to PCI Certification, LANL will engage a qualified Special Inspector to evaluate the structural precast concrete fabricator’s quality-control and testing methods.

Allow LANL’s Special Inspectors access to material storage areas, concrete production equipment, concrete placement, and curing facilities. Cooperate with Special Inspectors and provide samples of materials and concrete mixtures as may be requested for additional testing and evaluation.

Strength of precast structural concrete units will be considered deficient if units fail to comply with <<ACI CODE-318>> requirements for concrete strength.

      - ***************************************************************************************

      - Revise testing and acceptance criteria in first paragraph below if required. Revise to add criteria for load tests if required.

      - ***************************************************************************************

If there is evidence that strength of precast concrete units may be deficient or may not comply with <<ACI CODE-318>> requirements, employ a qualified testing agency to obtain, prepare, and test cores drilled from hardened concrete to determine compressive strength according to <<ASTM C42/C42M>>.

A minimum of three representative cores will be taken from units of suspect strength, from locations directed by EOR.

Cores will be tested in an air-dry condition or, if units will be wet under service conditions, test cores after immersion in water in a wet condition.

        - ******************************************************************************

        - PCI's recommendations in first subparagraph below are more stringent than ACI's.

        - ******************************************************************************

Strength of concrete for each series of 3 cores will be considered satisfactory if average compressive strength is equal to at least 85 percent of 28-day design compressive strength and no single core is less than 75 percent of 28-day design compressive strength.

Test results will be made in writing on same day that tests are performed, with copies to EOR, Subcontractor, and precast concrete fabricator. Test reports will include the following:

Project identification name and number.

Date when tests were performed.

Name of precast concrete fabricator.

Name of concrete testing agency.

Identification letter, name, and type of precast concrete unit(s) represented by core tests; design compressive strength; type of break; compressive strength at breaks, corrected for length-diameter ratio; and direction of applied load to core in relation to horizontal plane of concrete as placed.

Patching:  If core test results are satisfactory and precast structural concrete units comply with requirements, clean and dampen core holes and solidly fill with same precast concrete mixture that has no coarse aggregate, and finish to match adjacent precast concrete surfaces.

Defective Units:  Discard and replace precast structural concrete units that do not comply with requirements, including strength, manufacturing tolerances, and color and texture range.  Chipped, spalled, or cracked units may be repaired, subject to EOR's approval.  EOR reserves the right to reject precast units that do not match approved samples, sample panels, and mockups.

PART 3 - EXECUTION

EXAMINATION

Examine supporting structural frame or foundation and conditions for compliance with requirements for installation tolerances, true and level bearing surfaces, and other conditions affecting performance of the Work.

Proceed with installation only after unsatisfactory conditions have been corrected.

Do not install precast concrete units until supporting, cast-in-place, building structural framing has attained minimum allowable design compressive strength or until supporting steel or other structure is complete.

Topping slabs shall be placed on clean precast floor or roof to include removal of laitance.

INSTALLATION

Install clips, hangers, bearing pads, and other accessories required for connecting precast structural concrete units to supporting members and backup materials.

Erect precast structural concrete in accordance with the approved Erection Plan; and level, plumb, and square within specified allowable tolerances.  Provide temporary structural framing, supports, and bracing as required to maintain position, stability, and alignment of units until permanent connection.

Install temporary steel or plastic spacing shims or bearing pads as precast structural concrete units are being erected.  Tack-weld steel shims to each other to prevent shims from separating.

Maintain horizontal and vertical joint alignment and uniform joint width as erection progresses.

Remove projecting lifting devices and grout fill voids within recessed lifting devices flush with surface of adjacent precast surfaces when recess is exposed.

        - ******************************************************************************

        - Retain subparagraph below if voids of hollow-core slabs are used for electrical raceways or mechanical ducts.

        - ******************************************************************************

For hollow-core slab voids used as electrical raceways or mechanical ducts, align voids between units and tape butt joint at end of slabs.

        - ******************************************************************************

        - Retain subparagraph below if Project includes prestressed concrete.

        - ******************************************************************************

Tendons and post-tensioning ducts shall be placed within required tolerances and supported to prevent displacement beyond required tolerances during concrete placement.

        - ******************************************************************************

        - Retain subparagraph below if Project includes post-tensioned concrete.

        - ******************************************************************************

Couplers shall be placed in areas approved by the EOR and enclosed in housings long enough to permit necessary movements.

Connect precast structural concrete units in position by bolting, welding, grouting, or as otherwise indicated on Shop Drawings. Remove temporary shims, wedges, and spacers as soon as practical after connecting and grouting are completed.

Do not permit connections to disrupt continuity of roof flashing.

Field cutting of precast units is not permitted without approval of the EOR.

      - ***************************************************************************************

      - First paragraph below refers to fastening under the control of precast concrete erector. Coordinate with and repeat warning in other Sections if additional construction will be fastened to precast, prestressed concrete units.

      - ***************************************************************************************

Fasteners: Do not use drilled or powder-actuated fasteners for attaching accessory items to precast, prestressed concrete units.

Welding: Comply with applicable <<AWS D1.1/D1.1M>> and <<AWS D1.4/D1.4M>> for welding, welding electrodes, appearance, quality of welds, and methods used in correcting welding work.

Protect precast structural concrete units and bearing pads from damage by field welding or cutting operations, and provide noncombustible shields as required.

        - ******************************************************************************

        - Retain subparagraph below if Project includes prestressed concrete.

        - ******************************************************************************

Burning or welding operations in the vicinity of prestressing reinforcement shall be performed in such a manner that prestressing reinforcement is not subject to welding sparks, ground currents, or temperatures that degrade the properties of the reinforcement.

Clean weld-affected steel surfaces with chipping hammer followed by brushing, and apply a minimum 4.0-mil-thick coat of galvanized repair paint to galvanized surfaces according to <<ASTM A780/A780M>>.

        - ******************************************************************************

        - Retain subparagraph above or first subparagraph below.

        - ******************************************************************************

Clean weld-affected steel surfaces with chipping hammer followed by brushing, and re-prime damaged painted surfaces.

Remove, reweld, or repair incomplete and defective welds.

At bolted connections, use lock washers, tack welding, or other approved means to prevent loosening of nuts after final adjustment.

Where slotted connections are used, verify bolt position and tightness. For sliding connections, properly secure bolt but allow bolt to move within connection slot. For friction connections, apply specified bolt torque and check 25 percent of bolts at random by calibrated torque wrench.

      - ***************************************************************************************

      - In paragraph below, revise locations and extent of grouting if required.

      - ***************************************************************************************

Grouting: Grout connections and joints and open spaces at keyways, connections, and joints where required or indicated on Shop Drawings.  Retain grout in place until hard enough to support itself.  Pack spaces with stiff grout material, tamping until voids are completely filled.

Place grout to finish smooth, level, and plumb with adjacent concrete surfaces.

Fill joints completely without seepage to other surfaces.

Trowel top of grout joints on roofs smooth and uniform. Finish transitions between different surface levels not steeper than 1 to 12.

        - ******************************************************************************

        - Retain first subparagraph below if end grouting hollow-core slabs is required.

        - ******************************************************************************

Place grout end cap or dam in voids at ends of hollow-core slabs.

Promptly remove grout material from exposed surfaces before it affects finishes or hardens.

Keep grouted joints damp for not less than 24 hours after initial set.

ERECTION TOLERANCES

Erect precast structural concrete units level, plumb, square, true, and in alignment without exceeding the noncumulative erection tolerances of <<ACI ITG-7>> and, for precast concrete with cast-in-place concrete, <<ACI SPEC-117>>​.

Minimize variations between adjacent slab members by jacking, loading, or other method recommended by fabricator and approved by EOR.

FIELD QUALITY CONTROL

Testing Agency: Subcontractor shall engage a qualified testing agency to perform tests.

Field welds shall be visually inspected by a LANL-approved Certified Welding Inspector, and the inspections shall be documented in accordance with Section << 01 4455 - Onsite Welding, Brazing and Joining Requirements>>. Field welds shall also be nondestructively tested according to <<ASTM E165/E165M>> or <<ASTM E709>> as well as Section << 01 4455 - Onsite Welding, Brazing and Joining Requirements>>. High-strength bolted connections are subject to inspections.

Sand-cement and nonshrink grout compressive strength shall be tested in accordance with <<ASTM C109/C109M>>. Strength of grout is satisfactory if 28-day compressive strength is equal to or exceeds specified grout strength.

Testing agency will report test results within five (5) working days and in writing to Subcontractor and EOR.

Repair or remove and replace work where tests and inspections indicate that it does not comply with specified requirements.

In the event that repair/replacement (still) doesn’t comply with specified requirements, an Nonconformance Report (NCR) shall be generated to document the repair/replacement necessary to achieve compliance.

Additional testing and inspecting, at Subcontractor's expense, will be performed to determine compliance of replaced or additional work with specified requirements.

Prepare test and inspection reports.

REPAIRS

      - ***************************************************************************************

      - Blemishes occurring after delivery are normally repaired after erecting units. Repairs of production chips, cracks, and spalls take place at manufacturer's plant.

      - ***************************************************************************************

Repair precast structural concrete units if permitted by EOR.

Repairs may be permitted if structural adequacy, serviceability, durability, and appearance of units have not been impaired.

      - ***************************************************************************************

      - Precast concrete manufacturer develops appropriate repair mixtures and techniques during production sample approval process.

      - ***************************************************************************************

Mix patching materials and repair units so cured patches blend with color, texture, and uniformity of adjacent exposed surfaces and show no apparent line of demarcation between original and repaired work, when viewed in typical daylight illumination from a distance of << 20 feet>>.

Prepare and repair damaged galvanized coatings with galvanizing repair paint according to <<ASTM A780/A780M>>.

      - ***************************************************************************************

      - Retain paragraph above if using galvanized anchors, connections, and other items; retain first paragraph below if items are prime painted.

      - ***************************************************************************************

Wire brush, clean, and paint damaged prime-painted components with same type of shop primer.

Remove and replace damaged precast structural concrete units that cannot be repaired or when repairs do not comply with requirements as determined by EOR.

CLEANING

Clean mortar, plaster, fireproofing, weld slag, and other deleterious material from concrete surfaces and adjacent materials immediately.

Clean exposed surfaces of precast concrete units after erection and completion of joint treatment to remove weld marks, other markings, dirt, and stains.

Perform cleaning procedures, if necessary, according to precast concrete fabricator's written recommendations.  Protect other work from staining or damage due to cleaning operations.

Do not use cleaning materials or processes that could change the appearance of exposed concrete finishes or damage adjacent materials.

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 03 4100, REV. 4, DATED APRIL 15, 2026.