Section 05 2100 
Steel Joist Framing

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 7 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., SECTION INCLUDES in PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Structural POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General Requirements.

      - This specification section is for use with LANL ESM Chapter 5 - Structural, Section II; therefore it is applicable to ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality discussion.

      - ==========================================================

      - This specification section covers the requirements for steel joists and joist girders (referred to herein as joists), as well as associated accessories, fittings and priming/painting.  Aluminum joists, cold-formed steel-framed joists and trusses, and built-up structural-steel trusses are not covered.

      - LANL ESM Chapter 5 - Structural, Sect. II.7, references the International Building Code (IBC), Chapter 22, Steel, for guidance on design requirements for steel building structures, and components therein, most of which are contained in this and other sections in the Metals Division of the specifications

      - Industry standard practice requires that steel joist design is performed in coordination with the joist manufacturer, not solely by the Project’s Engineer of Record (EOR). The IBC and this Section template are written to reflect this requirement.

      - To enable the joist manufacturer to perform their portion of the joist design per SJI Specifications and project requirements, the IBC mandates that the Engineer of Record (EOR) indicate their design responsibilities on the construction drawings. This includes design criteria such as SJI joist designations, joist layout, load combinations, deviations from SJI Specs, lateral loads, and any special requirements. Some of these are covered in Article “Performance Requirements” of this Section. Refer to the “Design” paragraph in IBC Section 2207 for complete details.

      - For Seismic Design Category (SDC) D, to comply with IBC Section 2207.1.1, joists that are part of a seismic force-resisting system (SFRS) must be designed, detailed, fabricated, and erected in accordance with AISC 341. The only exception is for joists in non-building structures, provided that the response modification factor (R)  is such that use of AISC 360 is permitted.

      - For Seismic Design Category (SDC) C and response modification factor (R) less than 3, AISC 341 does not apply to joists that are part of the seismic force-resisting system (SFRS).

      - Joists are often subjected to axial loads from building lateral forces (e.g., acting as struts or ties between diaphragm chords, or within sub-diaphragms transferring wall-anchorage forces). The magnitude, source (W or E), and—if seismic—the type (E or Em) of these axial forces must be clearly communicated to the supplier.

  - *************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

      - ***************************************************************************************

      - Retain paragraphs below that apply to the project.

      - ***************************************************************************************

K-Series steel joists.

Long-span steel joists.

Joist girders.

      - ***************************************************************************************

      - Search all choice fields in this section with references to SJI 200 and SJI CJ COSP. Retain or select SJI 200 when CJ-series joists are specified for the Project. Remove or deselect all references to SJI 200 and SJI COSP when CJ-series joists are not used.

      - ***************************************************************************************

Composite steel joists (CJ-Series).

Joist accessories.

Cleaning​<< and shop painting; or  None - N/A>>​​.

RELATED REQUIREMENTS

Section << 01 4444 - Offsite Welding, Brazing and Joining Requirements>>.

Section << 01 4455 - Onsite Welding, Brazing and Joining Requirements>>.

Section << 09 9100 - Painting>>.

REFERENCE STANDARDS

ASTM A36/A36M - Standard Specification for Carbon Structural Steel.

ASTM A123/A123M - Standard Specification for Zinc (Hot-Dip Galvanized) Coatings on Iron and Steel Products.

ASTM A153/A153M - Standard Specification for Zinc Coating (Hot-Dip) on Iron and Steel Hardware.

ASTM A563/A563M - Standard Specification for Carbon and Alloy Steel Nuts (Inch and Metric).

ASTM A780/A780M - Standard Practice for Repair of Damaged and Uncoated Areas of Hot-Dip Galvanized Coatings.

ASTM B695 - Standard Specification for Coatings of Zinc Mechanically Deposited on Iron and Steel.

ASTM F436/F436M - Standard Specification for Hardened Steel Washers Inch and Metric Dimensions.

ASTM F3125/F3125M - Standard Specification for High Strength Structural Bolts and Assemblies, Steel and Alloy Steel, Heat Treated, Inch Dimensions 120 ksi and 150 ksi Minimum Tensile Strength, and Metric Dimensions 830 MPa and 1040 MPa Minimum Tensile Strength.

AWS D1.1/D1.1M - Structural Welding Code - Steel.

AWS D1.3/D1.3M - Structural Welding Code - Sheet Steel.

CAL (CDPH SM) - Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources Using Environmental Chambers Version 1.2.

MPI #18 - Primer, Zinc Rich, Organic.

MPI #19 - Primer, Zinc Rich, Inorganic.

RCSC - Specification for Structural Joints Using High-Strength Bolts.

SJI 100 - Standard Specifications for K-Series, LH-Series, and DLH-Series Open Web Steel Joists, and for Joist Girders.

SJI 200 - Standard Specifications for CJ-Series Composite Steel Joists.

SJI CJ COSP - Code of Standard Practice for CJ-Series Composite Steel Joists..

SJI COSP - Code of Standard Practice for Steel Joist and Joist Girders.

SJI Technical Digest No. 9 - Handling and Erection of Steel Joists and Joist Girders.

SSPC-Paint 15 - Steel Joist Shop Primer/Metal Building Primer.

SSPC-Paint 20 - Zinc-Rich Coating (Type I - Inorganic, and Type II - Organic).

SSPC-SP 2 - Hand Tool Cleaning.

SSPC-SP 3 - Power Tool Cleaning.

DEFINITIONS

For definitions and acronyms, refer to COE Glossary of Terms.

Special Joists: Steel joists or joist girders requiring modification by manufacturer to support non-uniform, unequal, or special loading conditions that invalidate <<SJI 100>> Load Tables or <<SJI 200>> Weight Tables, as applicable.

ACTION SUBMITTALS

Product Data: For each type of joist, accessory, and product.

Calculations: Manufacturer’s design in accordance with the construction documents and with << SJI 100; and  SJI 200>> Specifications.

The design calculations shall be prepared by the manufacturer’s professional engineer (PE) responsible for the product design, and shall have a cover letter bearing the seal and signature of this PE.

In addition, and as applicable, the design calculations shall include the following:

Bridging design that differs from  ​​<< SJI 100; and  SJI 200>>​​ Specifications, such as cantilevered conditions and net uplift.

Connection design for:

Connections that differ from ​<< SJI 100; and  SJI 200>>​  Specifications, such as flush-framed or framed connections.

Field splices.

Joist headers.

Joist Drawings:  Manufacturer’s placement plan(s) showing the joist products indicated on the construction documents to be used for field installation in accordance with same.  At a minimum, the placement plan(s) shall include the following:

Listing of applicable loads as stated on the construction documents and used in the design calculations as specified on same.

Profiles for joist configurations that differ from those defined by ​<< SJI 100; and  SJI 200>>​ Specifications.

Connection requirements for:

Joist supports.

Joist girder supports.

Field splices.

Bridging anchorage/attachments.

Live and total load deflection criteria for joist configurations that differ from those defined by ​<< SJI 100; and  SJI 200>>​ Specifications.

Size, location and connections for bridging.

Joist headers.

Certification: Manufacturer’s certificate of compliance stating that work was performed in accordance with the construction documents and with ​<< SJI 100; and  SJI 200>>​ Specifications.

      - ***************************************************************************************

      - Retain the following paragraph and applicable subparagraphs when welding, brazing or joining is required.

      - ***************************************************************************************

Per the requirements of ​​​​​​<< Section 01 4444 - Offsite Welding, Brazing and Joining Requirements; and  Section 01 4455 - Onsite Welding, Brazing and Joining Requirements>>​​​​​​, submit

        - ******************************************************************************

        - When offsite only, omit submittals below regarding onsite welding. For high risk applications such as ML-1 or ML-2, add submittals for “Weld Filler Material Control Procedures” and “Filler Material Certified Material Test Reports (CMTRs)” when required.  Add “Post-Weld Heat Treatment Procedures” when required.

        - For Onsite welding use of LANL WPS/PQR is the default; coordinate usage with the LANL CWI; no submittal required.

        - For Onsite, welders are tested by LANL who will produce WPQR and track continuity; this includes brazing, bonding, and fusing; no submittal required.

        - ******************************************************************************

Welding Procedure Specification (WPS) and supporting Procedure Qualification Record (PQR).

Welder Performance Qualification Records (WPQR) including continuity.

Inspector qualification records

Inspection procedures

Shop drawings with weld details/symbols

      - ***************************************************************************************

      - Retain the paragraph below when NDE is applicable.

      - ***************************************************************************************

Per the requirements of Section ​​​​<< 01 4525 - Non-Destructive Examination (NDE) Requirements>>​​​​, submit:

Inspector qualification records.

Inspection procedures.

      - ***************************************************************************************

      - Retain the paragraph below when applicable to project.

      - ***************************************************************************************

Sustainable Design Submittals:

Product Data:  For products having recycled content, documentation indicating percentages by weight of postconsumer and pre-consumer recycled content.  Include statement indicating cost for each product having recycled content.

Laboratory Test Reports for Credit IEQ 4.2: For primers, documentation indicating that products comply with the testing and product requirements of <<CAL (CDPH SM)>>.

      - ***************************************************************************************

      - Retain the following Article if required by the project.

      - ***************************************************************************************

INFORMATIONAL SUBMITTALS

      - ***************************************************************************************

      - Informational submittals must be limited to those necessary for adequate quality control. The importance of an item, or complexity, in the context of the project should determine whether or not a submittal is required.

      - Retain first paragraph below with qualification requirements in Section << 01 4000 - Quality Requirements - Non-Nuclear>>​ and as may be supplemented in Article "Quality Control".

      - The reason Manufacturer Certificates are not included in this Article (as is the case in the AIA MasterSpec template for steel joist framing) is because that submittal pertains to Manufacturer Qualifications, which is N/A herein. Refer to author note in Article "Quality Control".

      - ***************************************************************************************

Qualification Data: For ​<< manufacturer; or  manufacturer's professional engineer>>​.

      - ***************************************************************************************

      - Coordinate first paragraph below with qualification requirements in Section << 01 4000 - Quality Requirements - Non-Nuclear>>.

      - ***************************************************************************************

Mill Certificates: For each type of bolt.

Field quality-control reports.

QUALITY CONTROL

      - ***************************************************************************************

      - Quality control is contained herein, and is the responsibility of the Construction Subcontractor.

      - Quality assurance, which is required by IBC Ch, 17, is contained in the EOR’s Statement of Special Inspections (SSI), and is the responsibility of LANL (i.e., execution of the SSI). The SSI template is found in LANL ESM Chapter 16 - Building Code Program, Sect. IBC-IP, Attach. B.

      - SJI has a qualification/certification program for manufacturers (i.e., “SJI membership”). While there were no such members in NM at time of writing, LANL projects in the last 5-7 years (TRU Waste, RLUOB, Indoor Firing Facility, Tactical Training Facility) used only joists from an SJI manufacturer, so this requirement in generic master was retained.

      - Retain this Article if field welding is required (due to Welding Quals Para. herein). If retaining, also retain "WPQR" paragraph in "Action Submittals" Article. LANL ESM Chapter 13 - Welding, Joining & NDE and AWS state that welding qualifications remain in effect indefinitely unless welding personnel have not welded for more than six months or there is a specific reason to question their ability. Since SJI has its own requirements for welding procedures, shop welding does not follow LANL or AWS requirements.

      - ***************************************************************************************

Manufacturer Qualifications: A manufacturer certified by SJI to manufacture joists complying with applicable standard specifications and load tables in ​<< SJI 100; and  SJI 200>>​​ Specifications.

Manufacturer's responsibilities include providing professional engineering services for designing special joists to comply with performance requirements.

      - ***************************************************************************************

      - Coordinate the following paragraph with the “WPQR” paragraph in the Article Action Submittals. Select the applicable option and retain the appropriate subparagraph(s) where additional shop and/or field welding requirements apply. For additional details refer to and SJI Technical Digest 8 Welding of Open Web Steel Joists and Joist Girders the following webinar Updated Guidance for Safe Handling and Erection of Joists — Inside the New Edition of Technical Digest 9

      - ***************************************************************************************

Welder Qualifications:  Welding processes and welding operators qualified in accordance with << AWS D1.1/D1.1M; and  AWS D1.3/D1.3M>> and dated no more than << 12 months; or  ______>> before start of scheduled welding work. << Comply with the following additional requirements:; or  None - N/A>>

Shop: Refer to Section << 01 4444 - Offsite Welding, Brazing and Joining Requirements>>.

Field: Refer to Section ​​​<< 01 4455 - Onsite Welding, Brazing and Joining Requirements>>​​​.

DELIVERY, STORAGE, AND HANDLING

      - ***************************************************************************************

      - For additional Guidance for Safe Handling and Erection of Joists refer to the following webinar Updated Guidance for Safe Handling and Erection of Joists — Inside the New Edition of Technical Digest 9

      - ***************************************************************************************

Deliver, storage and handle joists as recommended in ​<< SJI 100; and  SJI 200>>​ Specifications and <<SJI Technical Digest No. 9>>.

Protect joists from corrosion, deformation, and other damage during delivery, storage, and handling.

      - ***************************************************************************************

      - Retain the following paragraph if the steel bearing plates that are specified in this Section will be installed in cast-in-place concrete or unit masonry.

      - If this Article is retained then, per the author note associated with the “Related Requirements” paragraph, LANL Master Spec Section templates ​​<< 03 3001 - Reinforced Concrete>>​​, ​​<< 04 2220 - Reinforced Unit Masonry>>​​, and/or ​​<< 05 1000 - Structural Steel Framing>>​​ may need to be edited in order for the Project Spec to be complete and coordinated.

      - ***************************************************************************************

Sequencing

Deliver steel bearing plates to be built into ​​​<< cast-in-place concrete; and  unit masonry>>​​​ construction.

PART 2 - PRODUCTS

PERFORMANCE REQUIREMENTS

      - ***************************************************************************************

      - Retain and edit the following paragraph if required by the project.

      - ***************************************************************************************

General Requirements:

        - ******************************************************************************

        - Mechanical and electrical layout drawings and specifications for ceiling suspensions should contain notes indicating that hanger loads between panel points in excess of 50 pounds shall have the excess hanger loads suspended from panel points.

        - The standard joist tables cannot be used verbatim when the depth of the joist is reduced near the ends to accommodate two-way top chord slopes in excess of l/8 inch per foot. Before using standard designations for these joists, the designer must verify the adequacy of the joist members.

        - ******************************************************************************

​<< _______>>​

      - ***************************************************************************************

      - Revise paragraph below as necessary if any of the IBC’s “special loads” apply (since such loads invalidate SJI load and weight tables). Indicate locations of special joists on Drawings and identify them as "special." SJI’s “Specifications” call for EOR to provide a loading diagram /schedule to facilitate joist manufacturer’s design of special joists. SJI’s Code of Standard Practice (COSP) includes an example of a load schedule. Per IBC, EOR must indicate whether to follow ASD or LRFD design method (here and/or on Drawings).

      - ***************************************************************************************

Structural Performance: Provide special joists and connections capable of withstanding design loads indicated.

Use ​​<< ASD; data are given at service-load level; or  LRFD; data are given at factored-load level>>​​.

        - ******************************************************************************

        - Retain the following subparagraph if applicable to the project.

        - ******************************************************************************

Design special joists to withstand design loads with live-load deflections no greater than the following:

          - **********************************************************************

          - Retain subparagraphs below, and edit them as appropriate, if the deflection criteria differ from those defined by the SJI Specs:

          - - Floors: L/360 for nominal (i.e., unfactored) live load (L)

          - - Roofs: Same as for floors if ceiling is plaster or stucco. L/240 for live load for all other ceilings.

          - Although the SJI Specs don’t indicate total load (D + L) deflection criteria , since the live load criteria are the same as those (“minimums”) in the IBC, it can be assumed that the total load criteria are too (i.e., L/240 for floors & for roofs supporting plaster or stucco ceilings, and L/180 for all other roof cases).

          - **********************************************************************

Floor Joists: Vertical live and total loads deflections of ​<< _______>>​, respectively, of the span.

Roof Joists: Vertical live and total loads deflections of ​<< _______>>​, respectively, of the span.

      - ***************************************************************************************

      - Insert other performance and design criteria that apply to special joists. Examples may include stress-level reduction for special joists that are part of a fire-resistance-rated assembly, Vibration requirements for Steel Joist Concrete Floors, and IBC’s “special considerations.”

      - ***************************************************************************************

<< _______>>

      - ***************************************************************************************

      - Retain the following Article if Project uses open-web K-series steel joists.

      - ***************************************************************************************

K-SERIES STEEL JOISTS

Manufacture steel joists of type indicated according to <<SJI 100>> with steel-angle top- and bottom-chord members, underslung ends, and parallel top chord.

        - ******************************************************************************

        - Standard K-Series Joists are designed for simple span uniform loading, which results in a parabolic moment (M) diagram for chord forces and a linearly-sloped shear (V) diagram for web forces. When non-uniform and/or concentrated loads are encountered the V and M diagrams required may be shaped quite differently and may not be covered by the V and M design envelopes of a standard K-Series Joist. When conditions such as this arise, a KCS-Series (K-Series Constant Shear) joist may be a good option. These joists can also be used to support uniformly loads.

        - Finally, given all of the above, use of these joists is recommended where collateral loads (dead loads other than the weight of the building) are anticipated, but their exact locations have not yet been determined.

        - ******************************************************************************

Joist Type: ​​​​<< K-series steel joists; and  KCS-series steel joists>>​​​​.

        - ******************************************************************************

        - Retain the applicable subparagraphs from the following two subparagraphs, as required by the project.

        - ******************************************************************************

Minimum End Bearing on Steel Supports: << Comply with SJI 100;  As shown on the drawings;  2-1/2 inches; or  ____ inches>>.

Minimum End Bearing on Concrete or Masonry Supports: << Comply with SJI 100;  As shown on drawings;  4 inches; or  ____ inches>>.

Finish: << Shop primed;  Unprimed, unfinished;  Galvanized; or  _______>>.

      - ***************************************************************************************

      - Retain the paragraph below if K-series joist substitutes are required.

      - A Joist Substitute supports uniform loads when the span is < 10’. For such short spans an open web configuration is impractical; thus, these joists consist of a solid member(s). The depth of the member(s) is just 2.5”, and the maximum total safe uniformly distributed load-carrying capacity of a Joist Substitute is 550 plf (ASD), and 825 plf (LRFD).

      - ***************************************************************************************

Steel Joist Substitutes: Manufacture according to , with steel-angle or -channel members.

      - ***************************************************************************************

      - Since a hole in a chord member reduces it cross-sectional area, the joist carrying capacity can be reduced. This must be considered by both the EOR and the manufacturer. SJI’s “Specifications” require sizes and locations of such holes to be clearly indicated on the EOR’s drawings.

      - ***************************************************************************************

Provide holes in chord members for connecting and securing other construction to joists<< , as indicated on drawings>>.

      - ***************************************************************************************

      - Retain either, or both, of the next two paragraphs if top-chord extensions are required. These extensions are used to support a variety of overhang conditions (in which one or both ends of joist must cantilever beyond its bearing seat). When extensions are specified, the EOR must consider bracing requirements.

      - SJI offers two types of top chord extensions: “S (Simple)” Type (addressed here) and “R (Reinforced)” Type (addressed under “Extended Ends” paragraph).

      - Since only the top-chord angles are extended in the “S” Type, it is the weaker of the two types; however, it is more economical.

      - ***************************************************************************************

Top-Chord Extensions: Extend top chords of joists with SJI's S Type top-chord extensions where indicated, complying with <<SJI 100>>.

      - ***************************************************************************************

      - In the “R” Type top-chord extension (i.e., extended end), the standard 2.5” end bearing depth is maintained over the entire length of the extension by extending the bearing-seat angle in addition to the top-chord angles.

      - The 2.5” extension depth can be increased if greater load-carrying capacity is required.

      - ***************************************************************************************

Extended Ends: Extend bearing ends of joists with SJI's R Type extended ends where indicated, complying with <<SJI 100>>​.

      - ***************************************************************************************

      - SJI's “Specifications” state that joists are provided with camber, and it lists approximate camber that varies according to top-chord length. Finally, it requires EOR to consider coordinating camber with adjacent framing. For roof joists, camber must also be coordinated with roof-slope requirements.

      - ***************************************************************************************

Camber joists << according to SJI 100;  as indicated on drawings; or  _______>>.

Equip bearing ends of joists with manufacturer's standard beveled ends or sloped end bearings if the joist slope exceeds ​<< 1/4 inch per foot (1:48)>>​.

      - ***************************************************************************************

      - Retain the following Article if Project uses either LH- or Deep LH (DLH)-series steel joists. LH-series joists may be used in floor or roof decks for spans through 96’; DLH-series joists are limited to use in roof decks for spans through 240’.

      - ***************************************************************************************

LONG-SPAN STEEL JOISTS

Manufacture steel joists according to <<SJI 100>>, with steel-angle top- and bottom-chord members, of joist type and end and top-chord arrangements << as follows.; or  as indicated on drawings.>>

        - ******************************************************************************

        - Omit "Joist Type," "End Arrangement," and "Top-Chord Arrangement" subparagraphs below if joist type and end and top-chord arrangements are indicated on Drawings.

        - ******************************************************************************

Joist Type: ​​<< LH-series steel joists; and  DLH-series steel joists>>​​.

        - ******************************************************************************

        - Retain the applicable subparagraphs from the following two subparagraphs, as required by the project.

        - ******************************************************************************

Minimum End Bearing on Steel Supports: << Comply with SJI 100;  As shown on drawings;  4 inches; or  ____ inches>>.

Minimum End Bearing on Masonry or Concrete Supports: << Comply with SJI 100;  As shown on the drawings;  6 inches; or  ____ inches>>.

Finish: << Shop primed;  Unprimed, unfinished;  Galvanized; or  _______>>.

        - ******************************************************************************

        - Retain one option in the subparagraph below for either LH- or DLH-series joists.

        - ******************************************************************************

End Arrangement: << Underslung; or  Square>>.

        - ******************************************************************************

        - LH- and DLH-series joists are available with top and bottom chords parallel, top chord pitched one way, or top chord pitched two ways. Pitching is to provide slope for roof drainage. SJI's load tables are based on a standard pitch of 1/8 inch per foot (1:96). Coordinate with roof-slope requirements.

        - ******************************************************************************

Top-Chord Arrangement: ​​​​<< Parallel;  Pitched  1/8 inch per foot (1:96), one way;  Pitched  1/8 inch per foot (1:96), two ways; or  _______>>​​​​.

      - ***************************************************************************************

      - Since a hole in a chord member reduces it cross-sectional area, the joist carrying capacity can be reduced. This must be considered by both the EOR and the manufacturer. SJI’s “Specifications” require sizes and locations of such holes to be clearly indicated on the EOR’s drawings.

      - ***************************************************************************************

Provide holes in chord members for connecting and securing other construction to joists<< , as indicated on drawings>>.

      - ***************************************************************************************

      - SJI's “Specifications” state that joists are provided with camber, and it lists approximate camber that varies according to top-chord length. Finally, it requires EOR to consider coordinating camber with adjacent framing. For roof joists, camber must also be coordinated with roof-slope requirements.

      - ***************************************************************************************

Camber joists << according to  SJI 100;  as indicated on drawings; or  _______>>.

Equip bearing ends of joists with manufacturer's standard beveled ends or sloped end bearings if the joist slope exceeds 1/4 inch per foot (1:48).

      - ***************************************************************************************

      - Retain this Article if Project uses steel joist girders. Joist Girders are open web steel trusses used as primary framing members. They are designed as simple spans supporting equally spaced concentrated loads for a floor or roof system. These loads are considered to act at the panel points of the girders.

      - ***************************************************************************************

JOIST GIRDERS

Manufacture joist girders according to <<SJI 100>>, with steel-angle top- and bottom-chord members, with end and top-chord arrangements << as follows:; or  as indicated on drawings.>>

        - ******************************************************************************

        - Retain the applicable subparagraphs from the following two subparagraphs, as required by the project.

        - ******************************************************************************

Minimum End Bearing on Steel Supports: << Comply with SJI 100;  As shown on drawings;  6 inch; or  _____ inch>>.

Minimum End Bearing on Masonry or Concrete Supports: << Comply with SJI 100;  As shown on the drawings;  6 inches; or  ____ inches>>.

Finish: << Shop primed;  Unprimed, unfinished;  Galvanized; or  _______>>.

        - ******************************************************************************

        - Omit "End Arrangement" and "Top-Chord Arrangement" subparagraphs below if end and top-chord arrangements are indicated on Drawings.

        - Retain one option in the "End Arrangement" subparagraph below. Bottom-chord extensions provided for lateral bracing of bottom chords of joist girders are manufacturer's standard unless design of this connection is detailed by the EOR.

        - ******************************************************************************

End Arrangement: << Underslung;  Underslung with bottom-chord extensions; or  Square>>.

        - ******************************************************************************

        - Joist girders are available with top and bottom chords parallel, top chord pitched one way, or top chord pitched two ways. Pitching is to provide slope for roof drainage. SJI's load tables are based on a standard pitch of 1/8 inch per foot (1:96). Coordinate with roof-slope requirements.

        - ******************************************************************************

Top-Chord Arrangement: << Parallel;  Pitched  1/8 inch per foot , one way;  Pitched  1/8 inch per foot , two ways; or  _______>>.

      - ***************************************************************************************

      - Since a hole in a chord member reduces it cross-sectional area, the joist carrying capacity can be reduced. This must be considered by both the EOR and the manufacturer. SJI’s “Specifications” require sizes and locations of such holes to be clearly indicated on the EOR’s drawings. Predrilled holes in chord members are needed if bolting wood nailers to top chords.

      - ***************************************************************************************

Provide holes in chord members for connecting and securing other construction to joist girders<< , as indicated on drawings>>.

      - ***************************************************************************************

      - SJI's “Specifications” state that joist girders are provided with camber, and it lists approximate camber that varies according to top-chord length. Finally, it requires EOR to consider coordinating camber with adjacent framing. For roof joists, camber must also be coordinated with roof-slope requirements.

      - ***************************************************************************************

Camber joist girders << according to SJI 100;  as indicated on drawings; or  _______>>.

Equip bearing ends of joists with manufacturer's standard beveled ends or sloped end bearings if the joist slope exceeds 1/4 inch per foot (1:48).

      - ***************************************************************************************

      - Retain the following Article if Project uses composite steel joists. See SJI CJ COSP Sect. 6, para. 6.1(c) for limitations (e.g., deck and concrete thickness, etc.).

      - ***************************************************************************************

COMPOSITE STEEL JOISTS

Manufacture composite steel joists of type indicated according to <<SJI 200>>, with steel-angle top- and bottom-chord members, and parallel top chord, and with << underslung; or  square>> ends.

        - ******************************************************************************

        - Retain the applicable subparagraphs from the following two subparagraphs, as required by the project. Minimum end bearing is dependent on the depth of the joist seat. If specifying a value in this paragraph, verify the value specified with the referenced SJI standard for composite joists.

        - ******************************************************************************

Minimum End Bearing on Steel Supports: << Comply with SJI 200;  As shown on drawings;  4 inches;  2-1/2 inches; or  ____ inches>>.

Minimum End Bearing on Masonry or Concrete Supports: << Comply with SJI 200;  As shown on the drawings;  6 inches;  4 inches; or  ____ inches>>.

Finish: << Shop primed;  Unprimed, unfinished;  Galvanized; or  _______>>.

      - ***************************************************************************************

      - SJI CJ requires that composite joists be furnished with camber and states that, unless otherwise specified, the camber will be based on the deflection associated with 100% of the non-composite unfactored dead load (i.e., due to joist, metal deck, bridging and concrete slab).

      - It also states that if additional camber (over that described above, for example, to achieve a level floor after composite dead and live loads are placed) is required, it must be identified by the EOR.

      - The EOR must consider coordinating camber with adjacent framing. For roof joists, camber must also be coordinated with roof-slope requirements.

      - ***************************************************************************************

Camber composite steel joists << according to SJI 200;  as indicated on drawings; or  _______>>.

      - ***************************************************************************************

      - Retain the following Article if shop priming is required. The primer referenced in the SJI Specs—SSPC-Paint 15—is suitable for protecting joists from corrosion for a limited time only (i.e., during delivery, storage, and erection, and until further protected by other construction or coatings).

      - Per SJI CJ, it is the norm for CJ-series joists to be furnished unprimed/unpainted to avoid interfering with the welding of studs to the top chord.

      - If joists in Project are to receive direct-applied sprayed fire-resistant materials (SFRM) then use of a primer must be coordinated with IBC’s SFRM requirements, inspections and tests. SJI recommends such joists be furnished unprimed.

      - Retain one of two "Primer" paragraphs below unless joists are required to be unprimed. Usually retain first paragraph. The SJI Specs reference SSPC-Paint 15. Retain second paragraph if requiring a special primer to be shop-applied (which should be considered if finish painting is required, or if joists will be subjected to high humidity levels).

      - Note that LANL Master Spec Section ​<< 09 9100 - Painting>>​ doesn’t include shop priming.

      - ***************************************************************************************

PRIMERS

Shop and Touch-Up Primer: <<SSPC-Paint 15>>, or manufacturer's standard shop primer complying with performance requirements in <<SSPC-Paint 15>>.

      - *** OR ***

Shop and Touch-Up Primer: Provide shop primer that complies with << _______>>.

      - ***************************************************************************************

      - Retain the following paragraph if applicable to the project.

      - ***************************************************************************************

Touch-Up Primer for Galvanized Surfaces:  << SSPC-Paint 20 Type I - Inorganic;  SSPC-Paint 20 Type II - Organic; or  _________>>.

      - ***************************************************************************************

      - Retain the following Article if required by the project.

      - ***************************************************************************************

JOIST ACCESSORIES

      - ***************************************************************************************

      - Retain one of three "Bridging" paragraphs below. Bridging refers to permanent bridging (vs. “erection bridging,” which is also referred to by SJI as “erection stability bridging”).

      - For K-, LH/DLH-, and CJ-series joists, SJI requires top- and bottom-chord bridging, which must consist of horizontal bridging, vertical bridging, and both (in some instances).

      - For JG-series joists, since the framing joists brace the top chord of the JG, only bottom-chord bracing is required (i.e., bridging isn’t used with JG-series).

      - Note that “bridging anchors” and “bridging termination connections” are not the same thing: the former is provided by manufacturer, while the latter is provided by the EOR.

      - ***************************************************************************************

Bridging: Provide bridging anchors and number of rows of ​​<< horizontal; or  diagonal>>​​ bridging of material, size, and type required by ​​<< SJI 100; and  SJI 200>>​​ specifications for type of joist, chord size, spacing, and span. Furnish additional erection bridging if required for stability.

      - *** OR ***

Bridging: Schematically indicated. Detail and fabricate according to ​​<< SJI 100; and  SJI 200>>​​ Specifications. Furnish additional erection bridging if required for stability.

      - *** OR ***

Bridging: Fabricate as indicated and according to  ​​<< SJI 100; and  SJI 200>>​​ Specifications. Furnish additional erection bridging if required for stability.

      - ***************************************************************************************

      - Retain paragraph below if joists bear on masonry or concrete construction.

      - ***************************************************************************************

Fabricate steel bearing plates from <<ASTM A36/A36M>> steel with integral anchorages of sizes and thicknesses indicated. ​<< Shop prime paint; or  Hot-dip zinc coat according to ASTM A123/A123M>>​.

      - ***************************************************************************************

      - Retain paragraph below if ceiling is directly attached to bottom of joists.

      - Ceiling extensions close the gap between the bottom chord and adjacent walls. The SJI Specs state, "Ceiling extensions shall be furnished to support ceilings which are to be attached to the bottom of the joists. They are not furnished for the support of suspended ceilings." The reason being suspended-ceiling hangers may be tied to any portion of the joist's web or top chord.

      - Finally, it should be noted that direct application of ceiling framing to joists without furring may lead to uneven ceilings because joist soffit elevations may vary.

      - ***************************************************************************************

Furnish ceiling extensions, either extended bottom-chord elements or a separate extension unit of enough strength to support ceiling construction. Extend ends to within 1/2 inch of finished wall surface unless otherwise indicated.

        - ******************************************************************************

        - Retain one option in subparagraph below.

        - ******************************************************************************

Finish: ​​​<< Plain, uncoated;  Hot-dip zinc coating according to  ASTM A153/A153M , Class C; or  Mechanically deposited zinc coating,  ASTM B695 , Class 50>>​​​.

      - ***************************************************************************************

      - Retain paragraph below if SJI Specs indicate high-strength bolts are required. The only applications for which SJI Specs explicitly require such bolts are 1) Steel Bearing Seat Attachments for deep LH/DLH-series joists, and 2) Bolted Bridging Connections for the DLH-series joists.

      - However, there are other applications which could necessitate the use of high-strength bolts: Field Splices of LH/DLH-, JG-, and CJ-series joists. The reason being, the SJI Specs required that bolted field splices be designed for the member force, but > 50% of the member strength.

      - ***************************************************************************************

High-Strength Bolts, Nuts, and Washers: <<ASTM F3125/F3125M>>, Type 1, heavy hex steel structural bolts; <<ASTM A563/A563M>> heavy hex carbon-steel nuts; and <<ASTM F436/F436M>> hardened carbon-steel washers.

        - ******************************************************************************

        - Retain one option in subparagraph below.

        - ******************************************************************************

Finish: ​​​<< Plain, uncoated;  Hot-dip zinc coating according to  ASTM A153/A153M , Class C; or  Mechanically deposited zinc coating,  ASTM B695 , Class 50>>​​​.

Welding Electrodes: Comply with AWS standards.

      - ***************************************************************************************

      - Retain paragraph below if galvanized bolts or bearing plates are included in this Section.

      - ***************************************************************************************

Galvanizing Repair Paint: ​​​<< MPI #18;  MPI #19;  SSPC-Paint 20; or  ASTM A780/A780M>>​​​.

Furnish miscellaneous accessories including splice plates and bolts required by joist manufacturer to complete joist assembly.

      - ***************************************************************************************

      - Retain next Article if shop cleaning is required with or without shop priming.

      - ***************************************************************************************

CLEANING​​<< AND FINISH; or  None - N/A>>​​

Clean and remove loose scale, heavy rust, and other foreign materials from fabricated joists and accessories by ​<< hand-tool cleaning,  SSPC-SP 2; or  power-tool cleaning, SSPC-SP 3>>​.

      - ***************************************************************************************

      - Retain paragraph below if priming is not permitted or is not permitted in selected locations. Standard fabrication practice is to prime paint joists except for CJ type.

      - ***************************************************************************************

Do not prime paint joists and accessories<< to receive sprayed fire-resistive materials; or  None - N/A>>.

      - ***************************************************************************************

      - Select the applicable finish and preparation options in the following three paragraphs.

      - Preparation techniques required for steel surfaces are described in SSPC SP Standards - Surface Preparation. Edit this paragraph as appropriate.

      - ASTM A123/A123M includes minimum coating thickness requirements for various categories of components, based on thickness of steel. For example: 1.7 oz/sq ft (530 g/sq m) corresponds to Coating Grade 75, or a coating thickness of 3.0 mils, applicable to most steel products ranging in thickness from 1/8 to 3/16 inch in thickness. 2.0 oz/sq ft (600 g/sq m) corresponds to Coating Grade 85, or a coating thickness of 3.3 mils, applicable to structural shapes, plate, strip, and bar ranging in thickness between 3/16 and 1/4 inch in thickness. If coating grade or thickness is not specified, standard (minimum) requirements of ASTM A123/A123M will govern.

      - ***************************************************************************************

​​<< Shop prime joists;  Leave joists unprimed;  Galvanize joists; or  _______>>​​ ​​<< as specified;  as indicated on drawings; or  None - N/A>>​​.

        - ******************************************************************************

        - Select the applicable options from the following three subparagraphs. Confirm compatibility of spray applied fireproofing to primed or un-primed surfaces.

        - ******************************************************************************

Do not prime surfaces that will be ​<< fireproofed;  field welded;  in contact with concrete; or  ____>>​.

Galvanize steel ​<< ledge angles;  anchors to secure joists; and  ________>>​.

Leave​<<  other;    ____; or  None - N/A>>​ steel members unprimed.

Prepare surfaces to be finished in accordance with ​<< SSPC-SP 2;  SSPC-SP 3; or  ____>>​.

Galvanizing:  Provide minimum ​<< 1.7 oz/sq ft; or  ____ oz/sq ft>>​ galvanized coating to <<ASTM A123/A123M>> requirements.

      - ***************************************************************************************

      - SSPC-Paint 15 requires the minimum paint film thickness in paragraph below. Verify that joist manufacturer complies with this minimum.

      - ***************************************************************************************

Apply one coat of shop primer to joists and joist accessories to be primed to provide a continuous, dry paint film not less than 1 mil thick.

PART 3 - EXECUTION

EXAMINATION

Examine supporting substrates, embedded bearing plates, and abutting structural framing for compliance with requirements for installation tolerances and other conditions affecting performance of the Work.

Proceed with installation only after unsatisfactory conditions have been corrected.

      - ***************************************************************************************

      - The requirements of OSHA Steel Erection Standard, 29 CFR Part 1926, Subpart R-Steel Erection, are included in the SJI Specs (i.e., all of the joist series included herein are “covered”).

      - ***************************************************************************************

INSTALLATION

Do not install joists until supporting construction is in place and secured.

Install joists and accessories plumb, square, and true to line; securely fasten to supporting construction according to << SJI 100; and  SJI 200>>Specifications, << SJI COSP; and  SJI CJ COSP>>, joist manufacturer's written instructions, and requirements in this Section

Before installation, Splice-connect all joists delivered in multiple pieces to Project site.

Space, adjust, and align joists accurately in location before permanently fastening.

Install temporary bracing and erection bridging, connections, and anchors to ensure that joists are stabilized during construction.

        - ******************************************************************************

        - SJI cautions that a rigid connection of bottom chord to column be made only after application of dead loads. Revise subparagraph below to suit Project. Insert other limitations as required.

        - ******************************************************************************

Delay rigidly connecting bottom-chord extensions to columns or supports until dead loads are applied

      - ***************************************************************************************

      - Retain paragraph below if field welding joists to steel bearing plates or steel framework.

      - Per SJI 100, Where K- Series, LH-Series and DLH-Series Joists and Joist Girders are used to provide lateral stability to the supporting member, the final connection shall be made by welding or as designated by the specifying professional. Similarly, per SJI 200, when CJ-Series joists are used to provide lateral stability to the supporting member, the final connection shall be made by welding or as designated by the specifying professional.

      - ***************************************************************************************

Field weld joists to supporting steel ​​​<< bearing plates; or  framework>>​​​. Coordinate welding sequence and procedure with placement of joists. Comply with AWS requirements and procedures for welding, appearance and quality of welds, and methods used in correcting welding work.

Shall be in accordance with <<AWS D1.1/D1.1M>> as required for the necessary/applicable welding.

      - ***************************************************************************************

      - Retain one of first two paragraphs below for bolting joists to steel framework. Retain first paragraph if mild-strength carbon-steel bolts are required; retain second if high-strength structural bolts are required. Mild-strength bolts (i.e., ASTM A307) are standard with SJI.

      - An example of when A325 bolts are likely required is connection of JG-series joists used to a structural steel frame. Per SJI’s Specifications, “Joist Girders are usually attached to the columns by bolting with two 3/4 inch diameter A325 bolts.”

      - Per SJI 100, Where K- Series, LH-Series and DLH-Series Joists and Joist Girders are used to provide lateral stability to the supporting member, the final connection shall be made by welding or as designated by the specifying professional. Similarly, per SJI 200, when CJ-Series joists are used to provide lateral stability to the supporting member, the final connection shall be made by welding or as designated by the specifying professional.

      - ***************************************************************************************

Bolt joists to supporting steel framework using carbon-steel bolts

      - *** OR ***

Bolt joists to supporting steel framework using high-strength structural bolts. Comply with <<RCSC>> specification for high-strength structural bolt installation and tightening requirements.

Install and connect bridging concurrently with joist erection, before construction loads are applied. Anchor ends of bridging lines at top and bottom chords if terminating at walls or beams.

FIELD QUALITY CONTROL

Testing Agency: Engage a qualified testing agency to perform tests and inspections.

Visually inspect field welds according to <<AWS D1.1/D1.1M>>.

Visually inspect bolted connections.

Prepare test and inspection reports.

PROTECTION

Repair damaged galvanized coatings on galvanized items with galvanized repair paint according to <<ASTM A780/A780M>> and manufacturer's written instructions.

      - ***************************************************************************************

      - Standard shop paint should not be considered a prime coat for a coating system and is not typically touched up.

      - ***************************************************************************************

Touchup Painting: Cleaning and touchup painting are specified in Section << 09 9100 - Painting>>.

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 05 2100, REV. 7, DATED APRIL 15, 2026.