Section 21 0523 
General-Duty Valves for Water-Based Fire-Suppression Piping

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 1 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Fire POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable specification sections from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality sections.

  - ************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

      - ***************************************************************************************

      - The following paragraphs are designer choices based on project-specific conditions.

      - ***************************************************************************************

Two-piece ball valves with indicators.

Bronze butterfly valves with indicators.

Iron butterfly valves with indicators.

Check valves.

Bronze OS&Y gate valves.

Iron OS&Y gate valves.

NRS gate valves.

Indicator posts.

Trim and drain valves.

RELATED Requirements

Section << 01 2500 - Substitution Procedures>>.

    - **********************************************************************************************

      - The codes/standards listed below are provided for reference only and are not listed within the body of this Section. It is a designer-choice to include these codes/standards.

      - <<NFPA 14>>

    - **********************************************************************************************

REFERENCE standards

ASME B1.20.1 - Pipe Threads, General Purpose, Inch.

ASME B16.1 - Gray Iron Pipe Flanges and Flanged Fittings: Classes 25, 125, and 250.

ASME B31.9 - Building Services Piping.

AWWA C508 - Swing-Check Valves for Waterworks Service, 2-In. Through 48-In. (50-mm Through 1,200-mm) NPS.

AWWA C509 - Resilient-Seated Gate Valves for Water Supply Service.

AWWA C606 - Grooved and Shouldered Joints.

FM (AG) - FM Approval Guide.

NFPA 13 - Standard for the Installation of Sprinkler Systems.

NFPA 14 - Standard for the Installation of Standpipe and Hose Systems.

UL (DIR) - Online Certifications Directory.

UL 262 - Gate Valves for Fire-Protection Service.

UL 312 - Check Valves for Fire-Protection Service.

UL 789 - Indicator Posts for Fire-Protection Service.

UL 1091 - Standard for Butterfly Valves for Fire-Protection Service.

UL 1091B - Outline of Investigation for System Control Ball Valves for Fire Protection Service.

DEFINITIONS

For definitions and acronyms, refer to COE Glossary of Terms.

EPDM: Ethylene-propylene diene monomer.

NBR: Acrylonitrile-butadiene, Buna-N, or nitrile rubber.

NRS: Non-rising stem.

OS&Y: Outside screw and yoke.

PTFE: Polytetrafluoroethylene.

SBR: Styrene-butadiene rubber.

ACTION SUBMITTALS

Product Data: Provide data on valves including manufacturers catalog information. Submit performance ratings, rough-in details, weights, support requirements, and piping connections.

INFORMATIONAL SUBMITTALS

Warranty: Submit manufacturer warranty and ensure that forms have been completed and registered with manufacturer.

Operation and Maintenance Data: Include manufacturer's descriptive literature, operating instructions, maintenance and repair data, and parts listings.

QUALITY ASSURANCE

Where listed products are specified, provide products listed, classified, and labeled by UL and/or FM as suitable for the purpose indicated.

DELIVERY, STORAGE, AND HANDLING

Use the following precautions during storage:

Maintain valve end protection and protect flanges and specialties from dirt.

Provide temporary inlet and outlet caps.

Maintain caps in place until installation.

Store valves in shipping containers and maintain in place until installation.

Store valves indoors and maintain at higher than ambient dew point temperature.

If outdoor storage is unavoidable, store valves off the ground in watertight enclosures.

Use the following precautions for handling:

Use sling to handle large valves, rigged to avoid damage to exposed parts.

Do not use operating handles or stems as lifting or rigging points.

PART 2 - PRODUCTS

GENERAL REQUIREMENTS

UL Listed: Provide valves listed in <<UL (DIR)>> under following headings and bearing UL mark:

Fire Main Equipment.

Indicator Posts, Gate Valve.

Valves.

Ball Valves, System Control.

Butterfly Valves.

Check Valves.

Gate Valves.

Sprinkler System & Water Spray System Devices.

Valves, Trim, and Drain.

FM Global Approved: Provide valves listed in <<FM (AG)>> under the following headings:

Automated Sprinkler Systems

Indicator posts.

Valves:

Gate valves.

Single check valves.

Miscellaneous valves.

ASME Compliance

<<ASME B16.1>> for flanges on iron valves.

<<ASME B1.20.1>> for threads on threaded-end valves.

<<ASME B31.9>> for building services piping valves.

Comply with <<AWWA C606>> for grooved-end connections.

Comply with <<NFPA 13>> for valves.

Valve Pressure Ratings: Not less than minimum pressure rating indicated or higher as required.

Valve Sizes: Same as upstream piping unless otherwise indicated.

Valve Actuator Types

Worm-gear actuator with handwheel for quarter-turn valves, except trim and drain valves.

Handwheel: For other than quarter-turn trim and drain valves.

Hand-lever: For quarter-turn trim and drain valves 2 NPS and smaller.

      - ***************************************************************************************

      - The following nine Articles are designer choices based on project-specific conditions.

      - ***************************************************************************************

TWO-PIECE BALL VALVES WITH INDICATORS

Manufacturers

FNW

Nibco

Reliable

Substitutions: << Alternate products may be accepted, follow Section 01 2500 - Substitution Procedures; or  Not permitted – No substitutions>>.

<<UL 1091B>> and <<FM (AG)>> standard listing for indicating valves (ball type).

Description

Minimum Pressure Rating: 175 psig

Body Design: Two piece.

Body Material: Forged brass or bronze.

Port Size: Full or standard.

Seat: PTFE.

Stem: Bronze or stainless steel.

Ball: Chrome-plated brass.

Actuator: Worm gear or traveling nut.

Supervisory Switch: Internal or external.

End Connections for Valves 1 NPS through 2 NPS: Threaded ends.

End Connections for Valves 2-1/2 NPS and larger: Grooved ends.

BRONZE BUTTERFLY VALVES WITH INDICATORS

Manufacturers

FNW

Reliable

<< _______>>.

Substitutions: << Alternate products may be accepted, follow Section 01 2500 - Substitution Procedures; or  Not permitted – No substitutions>>.

<<UL 1091>> and <<FM (AG)>> standard listing for indicating valves, (butterfly or ball type).

Description:

Minimum Pressure Rating: 175 psig.

Body Material: Bronze.

Seat: EPDM.

Stem: Bronze or stainless steel.

Disc: ​​<< Bronze;  Stainless steel; or  _______>>​​ ​​<< with EPDM coating;  _______; or  None - N/A>>​​.

Actuator: Worm gear or traveling nut.

Supervisory Switch: Internal or external.

End Connections for Valves 1 NPS through 2 NPS: Threaded ends.

End Connections for Valves 2-1/2 NPS and larger: Grooved ends.

IRON BUTTERFLY VALVES WITH INDICATORS

Manufacturers

FNW

Kennedy Valve

Nibco

Reliable

Substitutions: << Alternate products may be accepted, follow Section  01 2500 - Substitution Procedures; or  Not permitted – No substitutions>>.

<<UL 1091>> and <<FM (AG)>> standard listing for indicating valves (butterfly or ball type).

Description:

Minimum Pressure Rating: 175 psig.

Body Material: Cast or ductile iron with ​<< nylon;  EPDM;  epoxy;  polyamide; or  _______>>​ coating.

Seat: EPDM.

Stem: Stainless steel.

Disc: Ductile iron, ​<< nickel plated;  EPDM coated;  SBR coated; or  _______>>​.

Actuator: Worm gear or traveling nut.

Supervisory Switch: Internal or external.

Body Design: Grooved-end connections.

CHECK VALVES

Manufacturers

FNW.

Kennedy Valve

Nibco

Reliable.

<< _______>>.

Substitutions: << Alternate products may be accepted, follow Section 01 2500 - Substitution Procedures; or  Not permitted – No substitutions>>.

      - ***************************************************************************************

      - Retain only one of the two following options.

      - ***************************************************************************************

<<UL 312>> and <<FM (AG)>> standard listing for check valves.

      - *** OR ***

<<AWWA C508>> compliant check valves.

Description:

Minimum Pressure Rating: 175 psig.

Type: Center guided check valve.

Body Material: Cast iron, ductile iron.

Center guided check with elastomeric seal.

Hinge Spring: Stainless steel.

End Connections: Flanged, grooved, or threaded.

BRONZE OS&Y GATE VALVES

Manufacturers

FNW

Nibco

Reliable

<< _______>>.

Substitutions: << Alternate products may be accepted, follow Section 01 2500 - Substitution Procedures; or  Not permitted – No substitutions>>.

<<UL 262>> and <<FM (AG)>> standard listing for fire-service water control valves (OS&Y and NRS-type gate valves).

Description:

Minimum Pressure Rating: 175 psig.

Body and Bonnet Material: Bronze or brass.

Wedge: One-piece bronze or brass.

Wedge Seat: Bronze.

Stem: Bronze or brass.

Packing: Non-asbestos PTFE.

Supervisory Switch: External.

End Connections: Threaded.

IRON OS&Y GATE VALVES

Manufacturers

FNW

Kennedy Valve

Nibco

Reliable

<< _______>>.

Substitutions: ​<< Alternate products may be accepted, follow Section 01 2500 - Substitution Procedures; or  Not permitted – No substitutions>>​.

Listed and Body Marked: <<AWWA C509>>, <<FM (AG)>>, and <<UL 262>>.

Description:

Size: << As indicated on Drawings;  2.5 inch;  3 inch;  4 inch;  6 inch;  8 inch;  10 inch; or  _______>>.

End Connections: << Flanged;  Grooved;  Threaded; or  _______>>.

Maximum Working Pressure: << 175 psi;  200 psi;  300 psi; or  _______>>.

Working Temperature: << 32 to 175 ; or  _______>>degrees Fahrenheit.

Body and Bonnet Material: Cast or ductile iron.

Wedge: Cast or ductile iron, or bronze<< with elastomeric coating;  _______; or  None - N/A>>.

Stem: Brass, bronze, or stainless steel.

Packing: Non-asbestos PTFE.

Supervisory Switch: External.

NRS GATE VALVES

Manufacturers

FNW

Nibco

Reliable

<< _______>>.

Substitutions: << Alternate products may be accepted, follow Section 01 2500 - Substitution Procedures; or  Not permitted – No substitutions>>.

<<UL 262>> and <<FM (AG)>> standard listing for fire-service water control valves (OS&Y and NRS-type gate valves).

Description:

Minimum Pressure Rating: 175 psig.

Body and Bonnet Material: Cast or ductile iron.

Wedge: Cast or ductile iron<< with elastomeric coating;  _______; or  None - N/A>>.

Wedge Seat: Cast or ductile iron, or bronze<< with elastomeric coating;  _______; or  None - N/A>>.

Stem: Brass or bronze.

Packing: Non-asbestos PTFE.

Supervisory Switch: External.

End Connections: << Flanged;  Grooved;  Threaded; or  _______>>.

INDICATOR POSTS

Manufacturers:

American Flow Control

Kennedy Valve

Nibco

Mueller

<< _______>>

Substitutions: << Alternate products may be accepted, follow Section 01 2500 - Substitution Procedures; or  Not permitted – No substitutions>>.

<<UL 789>> and <<FM (AG)>> standard listing for indicator posts.

Description:

Type: ​<< Underground;  Pit;  Wall; or  _______>>​.

Base Barrel Material: ​<< Cast or ductile iron;  PVC; or  _______>>​.

Extension Barrel for Adjustable Length Indicator Posts: Cast or ductile iron.

Cap: Cast or ductile iron.

Operation: << Wrench;  Handwheel; or  _______>>.

TRIM AND DRAIN VALVES

Ball Valves

Manufacturers

Reliable

AFG Manufacturing

Argco

Viking

<< _______>>.

Substitutions: << Alternate products may be accepted, follow Section 01 2500 - Substitution Procedures; or  Not permitted – No substitutions>>.

Description:

Pressure Rating: << 175 psig;  250 psig;  300 psig; or  _______>>.

Body Design: Two piece.

Body Material: Forged brass or bronze.

Port Size: Full or standard.

Seat: PTFE.

Stem: Bronze or stainless steel.

Ball: Chrome-plated brass.

Actuator: Hand-lever.

End Connections for Valves 1 NPS through 2 NPS: Threaded ends.

PART 3 - EXECUTION

EXAMINATION

Confirm valve interior to be free of foreign matter and corrosion.

Remove packing materials.

Examine guides and seats by operating valves from the fully open position to the fully closed position.

Examine valve threads and mating pipe for form and cleanliness.

Examine mating flange faces for conditions that might cause leakage.

Check bolting for proper size, length, and material.

Verify gasket for size, defects, damage, and suitable material composition for service.

Replace all defective valves with new valves.

INSTALLATION

Install listed fire protection shutoff valves supervised-open, located to control sources of water supply except from fire department connections.

Install permanent identification signs indicating portion of system controlled by each valve.

Install check valve in water supply connections and backflow preventer at potable water supply connections.

Valves with threaded connections to have unions at equipment arranged for easy access, service, maintenance, and equipment removal without system shutdown.

Valves in horizontal piping installed with stem at or above the pipe center.

Position valves to allow full stem movement.

Install valve tags.

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 21 0523, REV. 1, DATED APRIL 15, 2026.