Section 22 0813 
Testing Piping Systems

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 13 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Pressure Safety/Mechanical POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable Sections from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see ESM Chapter 1 - General, Section Z10 Specifications and Quality topics.

      - ==========================================================

      - For pressure systems within the scope of the pressure safety program, comply with LANL ESM Chapter 17 - Pressure Safety, Section PS-REQUIREMENTS, 10.3 Pressure and Leak Testing.

      - For pressure systems within the scope of the pressure safety program and when connecting to existing piping, piping joints shall be leak tested in accordance with LANL ESM Chapter 17 - Pressure Safety, Section PS-REQUIREMENTS, 10.3 Pressure and Leak Testing paragraph B. Modifications to Existing Systems. For leak testing of radiological contaminated systems, see LANL ESM Chapter 17 - Pressure Safety, Section PS-REQUIREMENTS, 10.3 Pressure and Leak Testing paragraph C. Modifications to Radiological Contaminated Existing Systems. This includes the bagging of vacuum joints where bags are used to cover the joint to verify the joint is leak free as part of an initial service leak test of the joint. The bag is then evaluated using standard radiological processes to verify there is no contamination before the gas is removed.

  - *************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

Pressure testing of the following systems:

        - ******************************************************************************

        - The following subparagraphs are designer choices based on project-specific requirements.

        - ******************************************************************************

Fire protection piping (<<NFPA 13>>)

Plumbing piping (<<IAPMO (UPC)>>)

Natural gas piping

Service piping downstream of regulator stations or meters (<<NFPA 54>>)

Distribution piping (<<ASME B31.8>> / <<49 CFR 192>>)

Compressed air piping (Less than 150 psig design pressure, <<ASME B31.9>>​​)

Instrument air piping (Less than 150 psig design pressure, <<ASME B31.9>>)

Hydronic piping (heating hot water, chilled water, tower water, condenser water, make-up water, and equipment drains; <<ASME B31.9>>)

Steam and condensate building service piping (<<ASME B31.9>>)

Steam and condensate utility distribution piping (<<ASME B31.1>>)

Refrigerant piping (<<ASME B31.5>>)

Vacuum piping (outside the scope of LANL ESM Chapter 17 - Pressure Safety)

Laboratory gas piping (<<ASME B31.9>>)

Process Piping (<<ASME B31.3>>)

      - ***************************************************************************************

      - Div 11 spec sections are not in SpecLink and need to be downloaded from the Engineering Standards specification website to include in the specification package, as applicable.

      - Include Div 11 sections in the Article below, if applicable to the project. Include Section << 01 4216 - Definitions>>, if required.

      - ***************************************************************************************

RELATED REQUIREMENTS

Section << 01 3300 - Submittal Procedures>>.

Section << 01 3545 - Water Discharge Requirements>>.

Section << 01 4000 - Quality Requirements - Non-Nuclear>>.

Section ​<< 01 4216 - Definitions>>​.

Section 11 5311.12 - Glovebox Installation.

Section 11 5311.18 - Glovebox Atmosphere Regenerable Purification Systems.

Section << 21 1300 - Fire-Suppression Sprinkler Systems>>.

Section << 22 1100 - Facility Water Distribution>>.

Section << 22 1316 - Sanitary Waste and Vent Piping>>.

Section << 22 1413 - Facility Storm Drainage Piping>>.

Section << 22 1500 - Compressed-Air Systems>>.

Section << 23 1123 - Facility Natural-Gas Piping>>.

Section << 23 2113 - Hydronic Piping>>.

Section << 23 2215 - Steam and Condensate Heating Piping and Specialties>>.

Section << 23 2300 - Refrigerant Piping>>.

Section << 23 2500 - HVAC Water Treatment>>.

Section << 33 5100 - Natural Gas Distribution>>.

Section << 33 6300 - Steam Energy Distribution>> .

Section << 40 0504 - Process Piping>>.

REFERENCE STANDARDS

49 CFR 192 - Transportation Of Natural and Other Gas By Pipeline: Minimum Federal Safety Standards.

ASME B31.1 - Power Piping.

ASME B31.3 - Process Piping.

ASME B31.5 - Refrigeration Piping and Heat Transfer Components.

ASME B31.8 - Gas Transmission and Distribution Piping Systems.

ASME B31.9 - Building Services Piping.

ASME PCC-2 - Repair of Pressure Equipment and Piping.

ASTM E515 - Standard Practice for Leaks Using Bubble Emission Techniques.

ASTM E1003 - Standard Practice for Hydrostatic Leak Testing.

IAPMO (UPC) - Uniform Plumbing Code.

NFPA 13 - Standard for the Installation of Sprinkler Systems.

NFPA 24 - Standard for the Installation of Private Fire Service Mains and Their Appurtenances.

NFPA 54 - National Fuel Gas Code.

UL 404 - Gauges, Indicating Pressure, for Compressed Gas Service.

SUBCONTRACTOR REQUIREMENTS

Notify LANL Subcontract Technical Representative (STR) at least 24 hours (1 working day) in advance of testing to arrange for onsite inspection by LANL Inspector (a hold/witness point).

        - NOTE: LANL Owner’s Inspector shall be qualified per <<ASME B31.3>> Paragraph 340 and LANL’s Engineering Services Division. LANL shall act for DOE to designate Owner’s Inspectors or Designee.

For discharge requirements of water used for pressure testing, follow Section << 01 3545 - Water Discharge Requirements>>​.

Notify LANL STR immediately in the event of any accidental discharge.

SUBMITTALS

Submit the following in accordance with Section << 01 3300 - Submittal Procedures>>.

Action Submittals

        - ******************************************************************************

        - The subparagraphs below shall be selected as applicable to the project.

        - ******************************************************************************

Test plan for potable water, sanitary sewer, and other systems outside the scope of LANL ESM Chapter 17 - Pressure Safety.

Pressure and Leak Testing procedures

Material of construction

Sketch of the testing apparatus and connection locations

Sketch extents of system being tested

Test pressures and duration of tests

Test medium

Requirements for calibration of pressure gauges as applicable (calibration certificates to be provided with test reports)

Test plan for pressure systems in the scope of LANL ESM Ch. 17 - Pressure Safety.

Pressure and Leak Testing procedures

Material of construction

Sketch of the testing apparatus and connection locations

Sketch extents of system being tested

Design pressures

Test pressures, including permissible tolerance on test pressure range

Duration of pressure or leak test

Test medium

Requirements for calibration of pressure gauges as applicable (calibration certificates to be provided with test reports)

Method to exclude personnel from the area containing the system to be tested. Include distance that personnel must be away from the hazard.

Over-pressurization protection/prevention: Device make/model number, certification designation (e.g., “UV” stamp), pressure relief set pressure, point of installation in system, and calculation substantiating the selection.

Informational Submittals

Test Reports:  Submit within 10 working days of successful test. Include calibration reports for pressure gauges as applicable.

PART 2 - PRODUCTS

    - **********************************************************************************************

      - Digital gauges are allowed provided they provide at least the same accuracy and calibration as analog (mechanical) gauges.

      - Vacuum leak testing digital gauges shall bound by a decade — e.g., if the level of vacuum required for the testing is 100 microns, a digital gauge shall be accurate to 10 microns. Vacuum leak test digital gauges also require test gauge calibration [for LANL self-performed work, to LANL Policy P330-2 (LANL access only)].

    - **********************************************************************************************

MATERIALS

Furnish instruments, equipment, material, and labor necessary to conduct tests.

Calibrate testing equipment at reasonable intervals with devices of accuracy traceable to National Institute of Standards and Technology (NIST). Test pressure shall be within the calibration range.

Test gauges used shall be per <<IAPMO (UPC)>>​, Section 318.

Pressure gauges meeting <<UL 404>>​.

Gauges shall have tempered safety glass, plastic face, or shield; and blowout back or plug.

PART 3 - EXECUTION

FIELD QUALITY CONTROL

      - ***************************************************************************************

      - The following paragraph is a designer choice based on project-specific requirements.

      - ***************************************************************************************

Perform piping pressure test before water treatment, cleaning, or flushing to avoid possible discharge of chemicals due to pipe or joint failure during a pressure test. Refer to Section ​<< 23 2500 - HVAC Water Treatment>>​.

Barricade the area around the system to be tested to ensure personnel do not enter the area during the pressure test.

Preliminary leak testing is allowed per the code of record but must be defined in the test plan.

Personnel, including the personnel performing the test, shall not enter the evacuation zone (exclusion zone) while the system is being pressurized.  Leak testing is only allowed after the hold period for the test has been complete and the pressure reduced, as allowed by the code of record.

        - ******************************************************************************

        - ASME PCC-2 contains a calculation for both blast wave and fragmentation distances.  Blast shielding may be used to reduce the evacuation zone provided they are adequate for the application and protect from direct and indirect fragments.

        - ******************************************************************************

The evacuation zone (exclusion zone) for pressure systems with  energy greater than 1000 lbf-ft testing shall be determined per <<ASME PCC-2>>, Mandatory Appendix 501-II, and Mandatory Appendix 501-III, or equal.

All examination records (blank forms) and pressure and/or leak test plans must be complete (except for results) and submitted prior to testing.  Plans shall

Specify tolerances; for example, test pressure to be -0 +15 psig.

Provide a means for a controlled release of pressure, for example, using a vent or drain valve.  Removal of caps, plugs, or flanges to vent pressure is not allowed.

Submit completed Test Reports, after testing.

Relief devices and other protective measures shall be utilized to protect against over pressurization during the testing, per code of record requirements.  This is applicable to pneumatic, hydrostatic, and hydro-pneumatic testing.

Relief devices shall have a set pressure and capacity calculation to verify and prevent the system from exceeding the test pressure constraints of the code of record.

The relief device shall not be adjustable and shall be sealed at the required set pressure.

A vacuum breaker valve may be required to prevent a system from being exposed to external pressure.

Subcontractor shall calculate the required size of the relief or vacuum protection required.

      - ***************************************************************************************

      - See LANL ESM Chapter 17 - Pressure Safety, Section PS-REQUIREMENTS, paragraphs 8.11 Flexible Hoses, and 8.12 Flexible Hose Restraints for additional information.

      - ***************************************************************************************

Temporary test systems that use flexible hoses, hose restraints, and whip checks must meet the following requirements:

External Restraints: Flexible tubing and hoses over 12 in. and in service pressure greater than 150 psig must be constrained at both ends or shielded in case of end-connector failure. The maximum separation distance between flexible hose restraints must not exceed 6-ft. intervals

Internal Restraints: Flexible hoses that are self-arresting with an internal valve enclosed within each hose end do not require hose restraint because these hoses do not whip.

Piping being tested shall remain exposed until LANL Inspector has approved the test results.

Trenches may be backfilled between joints before testing to prevent movement of pipe during testing.  Ensure that thrust blocks are sufficiently hardened before testing.

Piping being tested shall not leak nor show any change in test pressure (with accommodation for atmospheric conditions as allowed) for duration specified unless otherwise noted.  It is required that the pressure supply source be closed and the gauges monitored during pressure or vacuum decay test to verify a leak free system. It is recommended for other types of tests.

Where any portion of piping system is to be concealed before completion, the portion shall be tested separately as specified for the entire system.

Ensure piping supports are in place.

Test pressure shall not exceed the maximum allowable test pressure for any vessel, pump, valves, or other component in the system.  Isolate system gages, sensors, and similar components from pressure tests so instruments and devices are not damaged.

      - ***************************************************************************************

      - The designer shall retain the hydrostatic and/or pneumatic testing instructions below as applicable.

      - ***************************************************************************************

Hydrostatic (Water) Testing

Use potable water as test medium. Do not fill system until the LANL STR has approved the source of water supply.

Provide vents at high points to release trapped air while filling system.

Provide drains at low points for complete removal of test liquid.

Follow <<ASTM E1003>> for detecting leaks​​​<< or use other enhanced detection methods like pressure decay or vacuum decay techniques;   and use other enhanced detection methods like pressure decay or vacuum decay techniques; or  None - N/A>>​.

After the test duration reduce pressure to design pressure and visually examine the system for leaks.

Drain system if there is a potential for freezing, e.g., no heat in building, coil in outside air stream, and similar situations.

Install vacuum breaker valves as necessary to prevent buckling of piping when draining system.

Pneumatic (Air) Testing– pneumatic testing is permitted where appropriate, with a maximum stored energy at test pressure less than or equal to 1000 lbf-ft.

        - ******************************************************************************

        - Request approval for testing when stored energy at test pressure is greater than 1000 lbf-ft in accordance with LANL ESM Chapter 17 - Pressure Safety, Section PS-REQUIREMENTS, paragraph 10.3. Stored energy may be calculated based on ASME PCC-2, Mandatory Appendix 501-II, Stored Energy Calculations for Pneumatic Pressure Test.

        - ******************************************************************************

Use clean, dry air or inert gas as the test medium. Air is prohibited for natural gas distribution pipe testing.

Prior to application of full air test pressure, apply a preliminary test of not more than 10 psig to reveal possible major leaks.

After preliminary test, raise pressure in stages not more than 25 percent up to full test pressure, allowing at least 10 minutes for equalization of strain and detection of major leaks at each intermediate stage. Hold final test pressure for time specified.

If test pressure is 25 psig or less, pressure can be raised in a single increment.

Use <<ASTM E515>>​ for detecting leaks<< and use other enhanced detection methods like pressure decay or vacuum decay techniques;   or  use other enhanced detection methods like pressure decay or vacuum decay techniques; or  None - N/A>>.

After the test duration​<< reduce pressure to design pressure and; or  None - N/A>>​ visually examine the system for leaks.

If piping does not pass test or leaks are found repair and retest as required by Article ​​<< 3.3; or  _______>>​​ Retesting.

Retesting is not required in cases where it does not include:

Addition, replacement, alteration, or relocation of any piping or pressure boundary

In any cases where piping is set up temporarily for exhibition purposes.

PRESSURE OR LEAK TESTING

      - ***************************************************************************************

      - When connecting to existing piping, piping joints shall be leak tested in accordance with the LANL ESM Chapter 17 - Pressure Safety, Section PS REQUIREMENTS, 10.3 Pressure And Leak Testing paragraph B. Modifications to Existing System

      - Qualified examiners are not required for code leak tests except when specified by the code, for example ASME B31.3 para. 345.8 Sensitive Leak Test, 345.2.4(b) Externally Pressured Piping, and B31.5 para. 538.4.3 Leak Test.

      - The designer has the discretion to require qualified examiners and examination procedures.

      - The following paragraphs are designer choices based on project-specific requirements.

      - Under paragraphs Fire Protection Piping, Plumbing Piping, and Natural Gas Piping, designer shall select subparagraphs relevant to the project.

      - ***************************************************************************************

Fire Protection Piping (<<NFPA 13>>)

Below Grade: Test with water per <<NFPA 24>> at a minimum of 200 psig, or at 50 psig in excess of the system working pressure, whichever is greater for 2 hours. Piping shall maintain test pressure +/- 5 psi for the duration of the test and there shall be no visible signs of leakage.

Above Grade: Refer to Section ​<< 21 1300 - Fire-Suppression Sprinkler Systems>>​, for above-ground piping testing requirements.

Plumbing Piping (<<IAPMO (UPC)>> Code of Record):

        - ******************************************************************************

        - Test pumped drain piping to 1.5 times operating pressure, 25 psig minimum. Typical domestic water and sanitary are:

          - Pneumatic option for Sanitary test is at 5 psig

          - Hydrostatic Domestic Water test is at 80 psig

          - Pneumatic option for Domestic Water test is at 50 psig

        - ******************************************************************************

Pumped Drain Piping: Test with water at << 25; or  _______>> psig for 2 hours.

Sanitary Waste and Vent Piping Within Building to Building Wall, including condensate drain line from cooling coils:  See Section << 22 1316 - Sanitary Waste and Vent Piping>>​, for test pressures and durations.

Sanitary Sewer Piping Beyond Building Wall:  See Section << 22 1316 - Sanitary Waste and Vent Piping>>, for test pressures and durations.

Potable Water Inside Building: See Section << 22 1100 - Facility Water Distribution>>, for test pressures and durations.

Potable Water Site Main to Building Backflow Preventer:  See Section << 22 1100 - Facility Water Distribution>>, for test pressures and durations

Non-potable Water: See Section ​<< 22 1100 - Facility Water Distribution>>, for test pressures and durations.

Stormwater Piping

See Section << 22 1413 - Facility Storm Drainage Piping>>, for test pressures and durations of piping within building and within 5 feet outside of the building.

Stormwater Piping Beyond 5 feet of Building: Completely fill system with water and let stand for at least 1 hour before inspection starts, then visually inspect to ensure that all joints are tight.

Natural Gas Piping

Service piping downstream of regulator stations or meters (<<NFPA 54>>)

See Section << 23 1123 - Facility Natural-Gas Piping>>, for test pressures and durations.

Distribution piping (<<ASME B31.8>> / <<49 CFR 192>>)

See Section << 33 5100 - Natural Gas Distribution>>​, for test pressures and durations.

Compressed Air Piping (Less than 150 psig design pressure, <<ASME B31.9>>)

See Section << 22 1500 - Compressed-Air Systems>>​, for test pressures and durations.

Instrument Air Piping (Less than 150 psig design pressure, <<ASME B31.9>>)

See Section << 22 1500 - Compressed-Air Systems>>, for test pressures and durations.

Hydronic Piping (heating hot water, chilled water, tower water, condenser water, make-up water, and equipment drains; <<ASME B31.9>>)

See Section << 23 2113 - Hydronic Piping>>, for test pressures and durations.

Steam and Condensate Building Services Piping (<<ASME B31.9>>):

See Section << 23 2215 - Steam and Condensate Heating Piping and Specialties>>, for test pressures and durations

Steam and Condensate Utility Distribution Piping Systems (<<ASME B31.1>>):

See Section << 33 6300 - Steam Energy Distribution>>, for test pressures and durations.

Refrigerant Piping (<<ASME B31.5>>):

See Section << 23 2300 - Refrigerant Piping>>, for leak and pressure test pressures, durations, and allowable methods.

Vacuum Piping (outside the scope of LANL ESM Chapter 17 - Pressure Safety):

Evacuate to 1mm Hg (1 Torr or 1000 microns) measured with an electronic manometer or thermocouple gauge.  After 2 hours, if vacuum level has risen to no higher than 2.5 mm Hg (2.5 Torr or 2500 microns), the leak test is acceptable.

      - ***************************************************************************************

      - Test ASME B31.9 laboratory gas piping between 1 to 1.25 times design pressure.  ASME B31.9 paragraph 937.4.5 requires the test pressure be maintained for a minimum of 10 minutes.

      - If the code of record for the lab gas is ASME B31.3 (e.g., if a flammable/toxic gas), then test per the following paragraph titled Process Piping (ASME B31.3)

      - ***************************************************************************************

Laboratory Gas Piping (<<ASME B31.9>>):

Test piping with oil-free, dry cylinder nitrogen at ​<< _______>>​ psig +/- ​<< _______>>​ psig, not to exceed 150 psig, per <<ASME B31.9>>, paragraph 937.4 for at least 10 minutes.

Process Piping (<<ASME B31.3>>):

See Section << 40 0504 - Process Piping>>​, for test pressures and durations.

RETESTING

If piping does not pass the test or leaks are found, locate leak, safely vent pressure, and then repair leaks.  Removal of caps, plugs, or flanges to vent pressure is not allowed.

Repair by tightening, repair, or replacement, as appropriate.  Make repairs to piping with new materials.  Caulking on screwed joints, cracks, or holes is not acceptable.

Where repairs or additions are made to the piping system pressure boundary following the pressure test, retest the affected piping.

Repeat retesting until satisfactory results are obtained.  Notify LANL STR at least 24 hours (1 working day) in advance to arrange for onsite witnessing by LANL Owner’s Inspector of the piping retesting (a hold/witness point).

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 22 0813, REV. 13, DATED APRIL 15, 2026.