Section 22 1100 
Facility Water Distribution

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 7 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top seisto bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Mechanical POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable Sections from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality sections

  - *************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

      - ***************************************************************************************

      - The following paragraphs are designer choices based on project-specific requirements.

      - ***************************************************************************************

Piping, Buried within the Building Envelope (within 5 feet of Building)

Piping Above Grade

Unions and Flanges

Ball, Butterfly, and Gate Valves

Swing Check Valves

Silent Check Valves

Pressure Reducing Valves (PRV)

Pressure Reducing Valves (PRV): 1/2" to 2"

Circulator Pump, Hot Water

Strainers

Hose Bibb (Wall Hydrant)

Backflow Preventer, Threaded Ends

Backflow Preventer, Flanged Ends

Pressure Gauge

Thermometer

related requirements

Section << 01 2500 - Substitution Procedures>>.

Section << 07 8400 - Firestopping>>.

Section << 22 0529 - Hangers and Supports for Plumbing Piping and Equipment>>.

Section ​<< 22 0554 - Identification for Plumbing,  HVAC, and Fire Piping and Equipment>>​.

Section << 22 0713 - Plumbing and HVAC Insulation>>.

Section << 22 0813 - Testing Piping Systems>>.

Section << 22 0816 - Disinfection of Potable Water Piping>>.

Section << 22 4200 - Plumbing Fixtures>>.

Section << 31 2000 - Earth Moving>>.

REFERENCE STANDARDS

ANSI/ASME A112.21.3M - Hydrants for Utility and Maintenance Use.

ASME B16.18 - Cast Copper Alloy Solder Joint Pressure Fittings.

ASME B16.22 - Wrought Copper and Copper Alloy Solder-Joint Pressure Fittings.

ASME B16.24 - Cast Copper Alloy Pipe Flanges, Flanged Fittings, and Valves: Classes 150, 300, 600, 900, 1500, and 2500.

ASME B16.51 - Copper and Copper Alloy Press-Connect Pressure Fittings.

ASME B40.100 - Pressure Gauges and Gauge Attachments.

ASME B40.200 - Thermometers, Direct Reading and Remote Reading.

ASSE 1013 - Performance Requirements for Reduced Pressure Principle Backflow Prevention Assemblies.

ASTM B32 - Standard Specification for Solder Metal.

ASTM B88 - Standard Specification for Seamless Copper Water Tube.

ASTM D2846/D2846M - Standard Specification for Chlorinated Poly(Vinyl Chloride) (CPVC) Plastic Hot- and Cold-Water Distribution Systems.

ASTM F493 - Standard Specification for Solvent Cements for Chlorinated Poly(Vinyl Chloride) (CPVC) Plastic Pipe and Fittings.

ASTM F645 - Standard Guide for Selection, Design, and Installation of Thermoplastic Water-Pressure Piping Systems.

AWS A5.8M/A5.8 - Specification for Filler Metals for Brazing and Braze Welding.

AWWA C105/A21.5 - Polyethylene Encasement for Ductile-Iron Pipe Systems.

AWWA C110/A21.10 - Ductile-Iron and Gray-Iron Fittings.

AWWA C111/A21.11 - Rubber-Gasket Joints for Ductile-Iron Pressure Pipe and Fittings.

AWWA C151/A21.51 - Ductile-Iron Pipe, Centrifugally Cast.

AWWA C153/A21.53 - Ductile-Iron Compact Fittings.

AWWA C600 - Installation of Ductile-Iron Mains and Their Appurtenances.

AWWA M23 - PVC Pipe—Design and Installation.

AWWA M41 - Ductile-Iron Pipe and Fittings.

IAPMO (UPC) - Uniform Plumbing Code.

MSS SP-67 - Butterfly Valves.

MSS SP-110 - Ball Valves Threaded, Socket-Welding, Solder Joint, Grooved and Flared Ends.

MSS SP-125 - Check Valves: Gray Iron and Ductile Iron, In-Line, Spring-Loaded, Center-Guided.

MSS SP-139 - Copper Alloy Gate, Globe, Angle, and Check Valves for Low Pressure/Low Temperature Plumbing Applications.

NFPA 24 - Standard for the Installation of Private Fire Service Mains and Their Appurtenances.

NFPA 70 - National Electrical Code.

NSF/ANSI 14 - Plastic Piping System Components and Related Materials.

NSF/ANSI 61 - Drinking Water System Components - Health Effects.

NSF/ANSI/CAN 372 - Drinking Water System Components - Lead Content.

SUBMITTALS

Action Submittals

Catalog data on pipe materials, pipe fittings, valves, circulator pump, and accessories.

        - ******************************************************************************

        - Retain the following submittal when circulator pumps are in project-scope.

        - ******************************************************************************

Submit shop drawings showing pump type, capacity, certified pump curves showing pump performance characteristics with pump and system operating point plotted. Include NPSH curve when applicable. Include electrical characteristics and connection requirements.

Installation instructions for pumps, valves, and accessories.

Informational Submittals

Field quality-control test reports.

Closeout Submittals

Operation and Maintenance Data: For water valves and specialties to include in emergency, operation, and maintenance manuals.

QUALITY ASSURANCE

      - ***************************************************************************************

      - The LANL-adopted UPC edition is per LANL ESM Chapter 16 - Building Code Program, IBC-GEN, Att. A (LBC)

      - ***************************************************************************************

Comply with the Uniform Plumbing Code, <<IAPMO (UPC)>>.

Piping materials shall bear label, stamp, or other markings of specified testing agency. Electrical Components, Devices, and Accessories: Listed and labeled as defined in <<NFPA 70>>​, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

      - ***************************************************************************************

      - The following paragraphs are a designer choice based on project-specific requirements.

      - ***************************************************************************************

Comply with <<NSF/ANSI 61>> for materials for water-service piping and specialties for domestic potable water.

Comply with <<NSF/ANSI 14>> for plastic potable-water-service piping.

Comply with <<ASTM F645>> for selection, design, and installation of thermoplastic water piping.

Comply with FM Group's "Approval Guide" or UL's  "Fire Protection Equipment Directory" for fire-service-main products.

NFPA Compliance: Comply with <<NFPA 24>>  for materials, installations, tests, flushing, and valve and hydrant supervision for fire-service-main piping for fire suppression.

PART 2 - PRODUCTS

PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section << 01 2500 - Substitution Procedures>>​.

      - ***************************************************************************************

      - The following PART 2 Articles are designer choices based on project-specific conditions. Within each Article, paragraphs related to pipe material types, fitting types, component size ranges, etc. are designer choices based on project-specific requirements.

      - ***************************************************************************************

PIPING, BURIED WITHIN THE BUILDING ENVELOPE (within 5 feet of building)

      - ***************************************************************************************

      - AWWA C151 available pipe size: 3-64 inches.

      - ***************************************************************************************

Ductile Iron Pipe: <<AWWA C151/A21.51>> .

Fittings: <<AWWA C110/A21.10>>, Ductile-Iron or Gray-Iron, Class 350, or <<AWWA C153/A21.53>>, Ductile Iron Compact Fittings, Class 350.

Joints: <<AWWA C111/A21.11>>, rubber gasket

Jackets: <<AWWA C105/A21.5>> polyethylene jacket

Copper Tubing: <<ASTM B88>>, <<NSF/ANSI 61>>, Type K, hard drawn or annealed.

Fittings: <<ASME B16.22>>.

Joints: Brazed, <<AWS A5.8M/A5.8>>, BCuP silver/phosphorus/copper alloy with melting range 1190 to 1480°F.

PIPING ABOVE GRADE

      - ***************************************************************************************

      - Specify Type K when design exceeds pressure and temperature ratings of Type L.

      - ***************************************************************************************

Copper Tubing: <<ASTM B88>>, <<NSF/ANSI 61>>, Type << L; or  K>>, hard drawn or annealed.

Fittings: <<ASME B16.22>> or <<ASME B16.51>>​.

Joints: <<ASTM B32>>​, Solder, Alloy Grade Sb5 tin-antimony, or Alloy Grade Sn95 tin and silver, with melting range 430 to 535°F.

CPVC Pipe and Fittings: <<ASTM D2846/D2846M>>, chlorinated polyvinyl chloride (CPVC) material for water service up to 180°F.

Joints: <<ASTM D2846/D2846M>>, solvent weld with <<ASTM F493>> solvent cement.

UNIONS and Flanges

Union for pipe 2 inches and under.

Copper Tubing: <<ASME B16.18>>, <<NSF/ANSI 61>> , lead free bronze, solder joint.

Dielectric Union for pipe 2 inches and under.

Manufacturer: Watts Model LF4001E.

Female iron pipe thread to solder connection, rated to 180 deg. F at 250 psi.  Less than 0.25% of lead by weight.

Flanges for pipe over 2 inches.

Copper Tubing: <<ASME B16.24>>, <<NSF/ANSI 61>>, Class 150, soldered or threaded.

Gaskets: 1/16-inch-thick preformed neoprene.

Ball, Butterfly, and Gate VALVES

Ball Valves up to 2 inches

Manufacturer: Nibco 585-66-LF (Lead Free) Series.

<<MSS SP-110>>, <<NSF/ANSI 61>> and <<NSF/ANSI/CAN 372>>, 600 psi non-shock cold working pressure (CWP), bronze, two-piece body, stainless steel vented ball, full port, Teflon seats, stainless steel stem, lever handle, solder or threaded ends to suit piping.

Butterfly Valves over 2 inches

Manufacturer: Nibco LD 2000–LF (Lead Free) Series.

<<MSS SP-67>>, <<NSF/ANSI 61>> and <<NSF/ANSI/CAN 372>>, 200 psi non-shock CWP, ductile iron body, aluminum bronze disc, resilient replaceable EPDM seat, lug style, extended neck, lever handle, for use between ANSI Class 125/150 flanges.

Gate Valves up to 2 inches

Manufacturer: Nibco 111-LF (Lead Free) Series.

<<MSS SP-139>>, <<NSF/ANSI 61>> and <<NSF/ANSI/CAN 372>>, 300 psig non-shock cold working pressure, Maximum 100 psig at 300 F, bronze body, bronze trim, rising stem, hand wheel, inside screw, solid wedge disc, soldered or threaded ends to suit piping.

Swing Check Valves

Sizes up to 2 inches

Manufacture: Nibco 413-LF (Lead Free) Series.

<<MSS SP-139>>, <<NSF/ANSI 61>> and <<NSF/ANSI/CAN 372>>, 200 psig non-shock cold working pressure, maximum 100 psig at 300 deg. F, bronze body, horizontal swing, Y pattern, renewable seat and disc. Solder or threaded ends to suit piping.

Silent check valve

Size up to 2 inches

Manufacturer: Nibco 480-LF (Lead Free) Series.

<<MSS SP-139>>, <<NSF/ANSI 61>> and <<NSF/ANSI/CAN 372>>, Class 125, bronze body, in line lift type, spring-actuated, TFE seat and disc, solder or threaded ends to suit piping.

Sizes over 2 inches:

Manufacturer: Nibco F-910-LF (Lead Free) Series.

<<MSS SP-125>>, <<NSF/ANSI 61>> and <<NSF/ANSI/CAN 372>> , Class 125, cast iron body, fluid to 200°F, renewable seats and disc, spring actuated, flanged. Use flat face flange and full-face gasket.

PRESSURE REDUCING VALVES (PRV)

      - ***************************************************************************************

      - Comply with LANL Mechanical Standard Detail ST-D2020 for PRV piping details.

      - ***************************************************************************************

Manufacturer: Cla-Val, Model No. ​<< 90-01AS; or  90-01AB>>​​​.

Single seated, hydraulically operated, pilot controlled, diaphragm type valve, 250 psi minimum pressure rating, 180 deg. F maximum water temperature and 15 to 75 psi adjustment range.

Pilot control: direct acting, adjustable, spring loaded, and normally open.

Valve construction: lead free, globe, ductile iron main valve body and cover, bronze main valve trim, and cast bronze pilot control with stainless steel trim. Repairs must be done without removing valve from line.

Optional Features: Flow Clean Strainer and CV Flow Control (opening speed control).

Optional Features: Flow Clean Strainer and shutoff cocks to isolate pilot system.

Capacity/Size

Flow: << _______>>  gpm.

Size: << _______>> inches with threaded ends (1” to 3”) or ASME B16.42 class 150 flanged ends (1-1/2” and larger).

Pressure Reducing valves (PRV): 1/2” to 2”

Manufacturers:

Cla-Val, CRD-L.  Cast bronze, low-lead CuZn21Si3P body and cover, stainless steel trim, reinforced EPDM diaphragm, EPDM rubber disc, and adjustment range << 15-65; or  ___>> psi.  Repair must be possible without removing valve from the line

Watts Regulator Company, No. << LF25AUB; or  LFU5B>>. Lead-free cast copper-silicon alloy body, stainless steel trim, integral strainer, 160°F maximum water temperature, bypass feature for thermal expansion, and approx. adjustments range << 25-75; or  _______>> psi. Repair must be possible without removing valve from line.

Capacity/Size

Flow: << _______>> gpm.

Size: << _______>> inches with NPT union inlet connection.

CIRCULATOR PUMP, HOT WATER

Manufacturer: Bell and Gossett, Series << 100; or  _______>>.

Cast iron or lead-free bronze body, polypropylene or lead-free brass impeller, steel shaft, suitable for 125 psi working pressure and 225°F water temperature, mechanical seal, direct drive, and oil lubricated drip proof motor, 1750 rpm.

Performance

Flow: << _______>> gpm at << _______>> feet head.

Electrical:<< _______>> hp, [     ] volts, << _______>> phase, 60 Hz.

Strainers

Sizes up to 3 inches

Manufacturer: Watts Series LF (Lead-Free) 777.

Lead free cast copper silicon alloy body and cap, <<NSF/ANSI 61>>, 300 psig at 210 F WOG, Y pattern with standard 20 mesh stainless steel screen, threaded or soldered connections.

Size over 2 inches

Manufacturer: Watts Series 77F-DI-FDA-125

Lead free per <<NSF/ANSI 61>>, Class 125 flanged cast iron body, 200 psi at 210 WOG, Y pattern with stainless steel perforated screen and drain/blowoff connection.

HOSE BIB (WALL HYDRANT)

Manufacturer: J.R. Smith Mfg. Co., Model 5609QT.

<<ANSI/ASME A112.21.3M>> , non-freeze, integral vacuum breaker, bronze or brass << nickel plated; or  None - N/A>>, 3/4-inch exposed hose connection, 1/4 turn, T-handle key.

      - ***************************************************************************************

      - BFPs: Comply with LANL Mechanical Standard Detail ST-D20GEN-1 sheet 1 for threaded end or sheet 2 for flanged ends for backflow preventer details. The LANL Utilities Group water system representative shall approve design and installation of backflow preventers installed outside the building (see Section 33 1000).

      - The BFP is required to be listed in UPC Table 603.2 Backflow Prevention Devices, Assemblies, and Methods, required by the application.

      - BFP for water service to boilers (hot water): The BFP is required to be rated to 250°F; see ASME BPVC Section IV HG-705 (c). This applies to both threaded and flanged ends. Designer shall edit the applicable paragraphs below to suit a BFP for water service to boilers when necessary.

      - For Section IV installation and IAMPO UPC compliance use an ASSE 1012, Backflow Preventers with an Intermediate Atmospheric Vent — or ASSE 1081, Backflow Preventers with Integral Pressure Reducing Boiler Feed Valve and Intermediate Atmospheric Vent Style for Domestic and Light Commercial Water Distribution Systems.

      - Suggested Manufacturers: Watts 9D; must meet ASSE 1012.

      - Additional items may be located using the IAPMO website search.

      - NOTE: BFP series listed below are for cold water service.

      - ***************************************************************************************

BACKFLOW PREVENTER, THREADED ENDS

Provide models listed in the latest edition of <<IAPMO (UPC)>> and compliant with <<NSF/ANSI 61>>.

<<IAPMO (UPC)>> Table 603.2 Backflow Prevention Devices, Assemblies, And Methods, specification <<ASSE 1013>>.

Suggested Manufacturers:

Zurn Wilkins, Series 975XL2U. Per <<ASSE 1013>>.

Watts, Series LF 909. Per <<ASSE 1013>>.

Assembly, reduce pressure type, lead free, bronze body, with ball type shutoff valves, FNPT ends, test cocks for in line field testing, integral unions between body and shut-off valves, and air gap drain funnel. Maximum water temperature range 33 to << 140; or  _______>> degrees F, maximum rated working pressure 150 psi.

Size: ​<< _______>>​ inch.

BACKFLOW PREVENTER, FLANGED ENDS

Provide models listed in the latest edition of <<IAPMO (UPC)>> and compliant with <<NSF/ANSI 61>>.

<<IAPMO (UPC)>> Table 603.2 Backflow Prevention Devices, Assemblies, And Methods, specification <<ASSE 1013>>.

Suggested Manufacturers:

Zurn Wilkins, Model 375AST. Per <<ASSE 1013>>.

Watts, Series LF 909. Per <<ASSE 1013>>.

Assembly, reduced pressure type, lead free, ductile or cast-iron body, with OS&Y shut-off valves, flanged ends, test cocks for in-line field testing, and an air gap drain funnel.  Maximum water temperature range 33 to << 140; or  _______>> degrees F, maximum rated working pressure 175 psi.

Size: ​<< ______>>​ inch.

PRESSURE GAUGE

      - ***************************************************************************************

      - Refer to manufacturer’s recommendation for gauge pressure ranges.  Generally, a pressure range of twice the expected normal pressure is recommended, with maximum working pressure not exceeding 75 percent of the range.  If pulsation occurs, working pressure should not exceed 65 percent of the pressure range.  Pressure gauges in the suction side of the pump will be vacuum pressure gauges.

      - ***************************************************************************************

Manufacturer: Ashcroft, Type 1009

<<ASME B40.100>>, Accuracy Grade 1A, maximum plus or minus 1 percent full scale accuracy, minimum 2-1/2 inch dial, stainless steel case, phosphor bronze bourdon tube and 1/4 inch NPT brass bottom connection.  Furnish with brass ball valve.

Range:<< _______>> to << _______>> psi or see Drawings.

THERMOMETER

Manufacturer: Reotemp, Model MM

<<ASME B40.200>>, Grade A, maximum plus or minus 1 percent full scale accuracy, bimetal thermometer, mercury free, minimum 4 inches dial, stainless steel case, all angle direct mount, with standard connection.

Range: << _______>> to << _______>> degrees F.

PART 3 - EXECUTION

PREPARATION

Ream pipe and tube ends.  Remove burrs.

Remove scale and dirt on inside and outside of pipe before assembly.

Keep open ends of pipe free from scale and dirt. Protect open ends with temporary plugs or caps.

      - ***************************************************************************************

      - Retain the following Article when buried piping is in project-scope.

      - ***************************************************************************************

BURIED PIPING

Provide earth cover, bedding, and warning tape per Drawings and Section << 31 2000 - Earth Moving>>.

INSTALLATION

Comply with Uniform Plumbing Code, <<IAPMO (UPC)>>, and as applicable with <<AWWA C600>>, <<AWWA M41>>, and <<AWWA M23>>.

Provide non-conducting dielectric connections wherever jointing dissimilar metals.

Route piping in orderly manner and maintain gradient.  Route parallel and perpendicular to walls

Install piping to maintain headroom and neither interfere with use of space nor take more space than necessary.

Group piping whenever practical at common elevations.

Install piping to allow for expansion and contraction without stressing pipe, joints, or connected equipment.

Provide access where valves and other equipment are not exposed.

Install valves with stems upright or horizontal, not inverted.

Pipe relief from safety valves and backflow preventers to nearest floor drain.

Slope water piping and provide drain valves at low points.

Sleeve and caulk pipes penetrating exterior walls or interior bearing walls.  Provide waterproof installation for exterior walls.  Provide UL/FM approved through-penetration firestop system when penetrating fire-rated barriers (e.g., walls, floors, etc.).

Paint exposed piping in occupied spaces to match background color.

Install chrome-plated steel escutcheons where pipes are not insulated in finished areas.

Provide stops on waterlines for plumbing fixtures. See Section << 22 4200 - Plumbing Fixtures>>.

Above Grade Piping: Provide ball valves or gate valves in piping 2 inches and smaller and butterfly valves in piping 2 1/2 inches and larger.  Provide globe valves for throttling application.

Support piping system in accordance with Section << 22 0529 - Hangers and Supports for Plumbing Piping and Equipment>>.

      - ***************************************************************************************

      - The following paragraph is a designer choice.

      - ***************************************************************************************

Sleeve and caulk pipes penetrating exterior walls or interior bearing walls. Provide waterproof installation for exterior walls. Provide UL/FM approved through-penetration firestop system when penetrating fire rated barriers (e.g., walls, floors, etc.). See Section << 07 8400 - Firestopping>>.

Disinfect water distribution system in accordance with Section << 22 0816 - Disinfection of Potable Water Piping>>​.

Pressure test piping system in accordance with Section ​​<< 22 0813 - Testing Piping Systems>>​​.

        - ******************************************************************************

        - Test piping to 1.5 times operating pressure, 100 psig minimum. Designer to include the three subparagraphs below as applicable to the project.

        - ******************************************************************************

Potable Water Inside Building: Test with water at ​​<< _______>>​​ psig for 30 minutes.

Potable Water Site Main to Building Backflow Preventer: Test with water at ​<< _______>>​ psig for 2 hours.

Non-potable Water: Test with water in accordance with the <<IAPMO (UPC)>> at ​<< _______>>​ psig for 30 minutes.

Label piping system in accordance with Section << 22 0554 - Identification for Plumbing,  HVAC, and Fire Piping and Equipment>>​.

Insulate piping system in accordance with Section << 22 0713 - Plumbing and HVAC Insulation>>.

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 22 1100, REV. 7, DATED APRIL 15, 2026.