Section 22 4200 
Plumbing Fixtures

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 8 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Mechanical/Architectural POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality sections.

  - *************************************************************************************************************

PART 1 - GENERAL

Section Includes

      - ***************************************************************************************

      - The following paragraphs are designer choices based on project-specific requirements.

      - ***************************************************************************************

Flush Valve Water Closets.

Flush Tank Water Closets.

Wall-Hung Urinals.

Lavatories.

Sinks.

Showers.

Electric Water Coolers.

Service Sinks.

Emergency Shower.

Emergency Eye and Face Wash.

Emergency Combination Shower with Eye and Face Wash.

Tepid Water Blending System (for emergency shower or wash stations).

RELATED SECTIONS

Section << 01 7700 - Closeout Procedures>>.

Section << 01 7823 - Operation and Maintenance Data>>.

Section ​<< 07 9200 - Joint Sealants>>​.

reference standards

ABA Standards - ABA Accessibility Standards.

ANSI Z358.1 - American National Standard for Emergency Eyewash and Shower Equipment.

ASME A112.6.1M - Floor-Affixed Supports for Off-the-Floor Plumbing Fixtures for Public Use.

ASME A112.18.1 - Plumbing Supply Fittings.

ASME A112.19.1 - Enamelled Cast Iron and Enamelled Steel Plumbing Fixtures.

ASME A112.19.2 - Ceramic Plumbing Fixtures.

ASME A112.19.3 - Stainless Steel Plumbing Fixtures.

IAPMO Z124 - Plastic Plumbing Fixtures.

IAPMO/ANSI Z124.5 - Plastic Toilet Seats.

NSF/ANSI 61 - Drinking Water System Components - Health Effects.

ACTION SUBMITTALS

Product Data: Submit catalog illustrations of fixtures, sizes,​<< rough-in dimensions,; or  None - N/A>>​ utility sizes, trim, and finishes.

Manufacturer's Installation Instructions: Submit installation methods and procedures.

Manufacturer's Certificate: Certify products meet or exceed specified requirements (e.g., flow test).

INFORMATIONAL SUBMITTALS AT CLOSEOUT

Submit in accordance with Section << 01 7700 - Closeout Procedures>>​.

Operation and Maintenance Data: Submit fixture, trim, exploded view and replacement parts lists. See Section << 01 7823 - Operation and Maintenance Data>>.

QUALITY ASSURANCE

Provide products requiring electrical connections listed and classified by a nationally recognized testing laboratory (e.g., Underwriters Laboratories Inc.) as suitable for purpose specific and indicated.

Provide ABA-compliant products.

Provide water conserving fixtures and fittings complying with the Uniform Plumbing Code or exceeding UPC where noted.

Comply with <<ABA Standards>> for mounting heights and locations of Plumbing Fixtures

      - ***************************************************************************************

      - Coordinate plumbing fixture selections with the Architect regarding casework, handicapped approach, ABA requirements if applicable.

      - All PART 2 Articles below are designer choices based on project-specific conditions.

      - ***************************************************************************************

PART 2 - PRODUCTS

FLUSH VALVE WATER CLOSETS

      - ***************************************************************************************

      - Low voltage flushometers (24Vac) may be used in new construction. Consult with the FOD. Retain only one of the two bowl options below.

      - ***************************************************************************************

Wall Hung Bowl: <<ASME A112.19.2>>; white, wall hung, vitreous china closet bowl, with elongated rim, 1-1/2 inch top spud, china bolt caps.

Manufacturer: Kohler, Model K-4325-0, Kingston.

      - *** OR ***

Floor Mounted Bowl: <<ASME A112.19.2>>; white, floor mounted, vitreous china closet bowl with elongated rim.

Manufacturer: Kohler, Model K-96053-0, Wellcomme Ultra

Sensor-Operated Flush Valve: <<ASME A112.18.1>>, concealed, diaphragm type with battery operated solenoid operator, infrared sensor and over-ride button in chrome plated plate, wheel handle stop and vacuum breaker; maximum ​​<< 1.28 gpf, wall mount; or  1.6 gpf, floor mount>>​​ gallon flush volume.

Manufacturer: Sloan, Model 8111–​<< 1.28, wall mount bowl; or  1.6, floor mount bowl>>​, G2 Optima Plus.

Seat: <<IAPMO/ANSI Z124.5>>, Solid white plastic, elongated open-front, self-sustaining hinge, stainless steel hardware, without cover.

Manufacturer: Kohler, Model K-4670-C.

      - ***************************************************************************************

      - Retain the following paragraph only when specifying Wall Hung Bowl above.

      - ************************************************************************************

Wall Mounted Carrier: <<ASME A112.6.1M>>​; adjustable cast iron frame, integral drain hub and vent, adjustable spud, lugs for floor and wall attachment, threaded fixture studs with nuts and washers.

FLUSH TANK WATER CLOSETS

      - ***************************************************************************************

      - Use floor-mounted flush tank water closets only in existing facilities when replacing fixtures of this type.

      - ***************************************************************************************

Pressure Light Toilet: <<ASME A112.19.2>>; white, floor mounted, vitreous china closet bowl, with elongated rim. Pressure flush, 1.6 gpf.

Manufacturer: Kohler, Model K-3505-TR, Wellworth.  Includes:

Toilet Bowl : Kohler, Model K-4303.

Toilet Tank: Kohler, Model K-4645-TR.

Tank cover, trip lever, tank accessory pack, bolt cap accessory pack

Seat: Solid white propylene plastic, elongated open-front, stainless steel hinge arms and hardware, without cover.

Manufacturer: Kohler, Model K-4731-C, Stronghold.

Angle Supply with Stop (single)

Manufacturer: Kohler, Model K-7637-CP.

WALL-HUNG URINALS

      - ***************************************************************************************

      - Low voltage flushometers (24Vac) may be used in new construction. Consult with the FOD.

      - ***************************************************************************************

Urinal: <<ASME A112.19.2>>; vitreous china, wall hung, washout urinal with shields, integral trap, removable stainless steel strainer, and 3/4 inch top spud, steel supporting hanger. Urinal shall use 0.125 gallon per flush.

Manufacturer: Kohler, Model K-4991-ET, Bardon.

Sensor Operated Flush Valve: <<ASME A112.18.1>>; exposed chrome plated, diaphragm type with battery operated solenoid operator, infrared sensor and over-ride button in chrome plated plate; maximum 0.125 gallon flush volume.

Manufacturer: Sloan, Model 8186-0.125, Optima Plus.

LAVATORIES

      - ***************************************************************************************

      - Low voltage faucets (24Vac) may be used in new construction. Consult with the FOD. Designer shall retain only one of the two lavatory options below.

      - ***************************************************************************************

Vitreous China Wall Hung Lavatory: <<ASME A112.19.2>> ; vitreous china wall mount lavatory, with 4 inch high back, 21 x 18 inches with drillings on 4 inch centers, rectangular basin with splash lip and front overflow.

Manufacturer: Kohler, Model K-2005 (4 inch centers), Kingston.

      - *** OR ***

Vitreous China Countertop Lavatory: <<ASME A112.19.2>>; vitreous china self-rimming countertop lavatory, 20 1/4 x 17 1/2 inches with drillings on 4 inch centers, front overflow, seal of putty, caulking, or concealed vinyl gasket.

Manufacturer: Kohler, Model K-2196-4, Pennington.

      - ***************************************************************************************

      - Metered faucets are not suitable for use with electric, tankless water heaters. Coordinate with water heater specification

      - ***************************************************************************************

Metered Faucet: <<ASME A112.18.1>>; chrome-plated, metered mixing faucet, maximum  0.25 gallons per use, 30 second automatic shut off, battery-operated solenoid operator and infrared sensor, aerator, trim plate, open grid strainer, back check for hot and cold supply, and thermostatic mixing valve.

Manufacturer: Sloan, Model EBF-85-A, Optima Plus.

Accessories:

Chrome plated 17-gage brass P-trap with clean-out plug and arm with escutcheon.

Chrome plated rigid supplies to fixtures with chrome plated brass  << loose key;  screwdriver; or  wheel handle>> stops, reducers, and escutcheons.

Offset waste with perforated open strainer.

Trap and waste insulated and offset to meet ABA compliance.

Wall Mounted Carrier: <<ASME A112.6.1M>>; cast iron and steel frame with tubular legs, lugs for floor and wall attachment, concealed arm supports, bearing plate and studs.

SINKS

      - ***************************************************************************************

      - The following are example specifications of different types of sinks. Edit accordingly to suit project. Designer shall retain only one of the three sink bowl options below.

      - ***************************************************************************************

Single Compartment Bowl: <<ASME A112.19.3>>, Commercial Grade, << _______>> x << _______>> x << _______>>  inch outside dimensions, 18 gage, Type 304 stainless steel. Self-rimming and undercoated, with 1-1/2 inch chrome brass drain, 3-1/2 inch crumb cup and chrome brass tailpiece, ledge back drilled for trim.

Manufacturer: Elkay, Model << _______>>.

      - *** OR ***

Double Compartment Bowl: <<ASME A112.19.3>>, Commercial Grade, ​<< _______>>​ x ​<< _______>>​ x ​<< _______>>​  inch outside dimensions 18 gage, Type 304 stainless steel. Self-rimming and undercoated, with 1-1/2 inch chrome brass drain, 3-1/2 inch crumb cups and chrome brass tailpiece, ledge back drilled for trim.

Manufacturer: Elkay, Model << _______>>.

      - *** OR ***

Enameled Bowl: <<ASME A112.19.1>> , white, cast iron, porcelain enameled double (equal) compartment, 32 x 22 inch outside dimensions, self-rimming and undercoated, with 4 hole faucet drilling, 3-1/2 inch diameter crumb cup, chrome brass tailpiece, and ledge back drilled for.

Manufacturer: Kohler, Model 5942-4, Brookfield.

Faucet: <<ASME A112.18.1>> ; chrome plated brass supply with swing spout, aerator with maximum 2.0 gpm flow, indexed lever handles.

Manufacturer: Kohler, K-7304-K, Triton.

Accessories:

Chrome plated 17-gage brass P-trap with clean-out plug and arm with escutcheon. Kohler Model K-8998.

Chrome plated rigid supplies to fixtures with chrome plated brass << loose key;  screwdriver; or  wheel handle>> stops, reducers, and escutcheons. Kohler Model K-7605.

SHOWERS

      - ***************************************************************************************

      - The following two paragraphs are designer choices.

      - ***************************************************************************************

Wheelchair Accessible Cabinet: <<IAPMO Z124>>; reinforced glass fiber, 36 x 36 x 80 inch high, soap dish, integral seat << left hand; or  right hand>>, grab bars, removable chrome plated strainer, tail piece, << _______>> color.

Manufacturer: Florestone, Model << 3PC44-52H; or  ___>>.

Shower Valve: Concealed shower supply, pressure balanced, anti-scald, brass body, with single lever handle, ceramic disc cartridge, integral stops, with flow control and adjustable spray ball joint showerhead with maximum 2.0 gpm flow, and escutcheon, hand held shower, 70 inch metal-clad shower hose and 24 inch slide bar, female inlet and vacuum breakers.

Manufacturer: Delta Monitor T-17230 with Delta Model 53001-DS Slide bar/Grab bar.

Regular Cabinet: <<IAPMO Z124>>; reinforced glass fiber, 36 x 37-1/2 x 73 inch high, removable chrome plated strainer, tailpiece, ​<< white; or  _______>>​ color.

Manufacturer: Florestone, Model 36-3WTB.

Shower Valve: Concealed shower supply, pressure balanced, anti-scald, brass body, with single lever handle, ceramic disc cartridge, integral stops, bent shower arm with flow control and adjustable spray ball joint showerhead with maximum 2.0 gpm flow, and escutcheon.

Manufacturer: Delta Monitor T-17230.

ELECTRIC WATER COOLERS

Water Cooler

        - ******************************************************************************

        - Other vinyl cabinet colors are available at no extra cost. Stainless steel units are available at an extra charge.

        - Elkay coolers shown are GreenSpec-designated; EPA Comprehensive Procurement Guidelines do not indicate electrical water coolers are to be Energy Star.

        - ******************************************************************************

Lead-free materials, handicapped wall mounted electric water cooler with stainless steel top and stainless steel cabinet, elevated anti-squirt bubbler with stream guard, bottle filler, automatic stream regulator, mounting bracket, energy efficient cooling system.

Capacity: 8 gph of 50 degrees F water, based upon 80 degrees F inlet water and 90 degrees F ambient.

          - **********************************************************************

          - Both options below may be applicable to a project.

          - **********************************************************************

Manufacturer: Elkay, Model EZSG8WSLK (High Efficiency Single Station).

Manufacturer: Elkay, Model EZSTL8WSLK (High Efficiency Dual Station).

UL listed in accordance with <<NSF/ANSI 61>>​ Section 9.

Electrical: Provide with electric cord and 3 prong rubber plug.

Accessories

Chrome plated 17-gage brass P-trap with clean-out plug and arm with escutcheon.

Chrome plated rigid supplies to fixtures with chrome plated brass << loose key;  screwdriver; or  wheel handle>> stops, reducers, and escutcheons.

Wall Carrier: Elkay Model << MLP100, single station; or  MLP200, dual station>>.

SERVICE SINKS

      - ***************************************************************************************

      - Designer shall retain only one of the two service sink bowl options below.

      - ***************************************************************************************

Bowl: <<ASME A112.19.1>>; 22 x 18 x 12 inch deep, white porcelain enameled (inside only) cast iron roll-rim sink, with 12 inch high back, concealed hanger, chrome plated strainer, stainless steel rim guard, cast iron ​​<< 2; or  3>>​​ inch P-trap with adjustable floor flange.

Manufacturer: Kohler, K-6714, Bannon, Service Sink, << K-6672, 2 inch P-Trap; or  K-6673, 3 inch P-Trap>>.

      - *** OR ***

Bowl: ​<< 36 x 24 x 10 inch; or  24 x 24 x 10 inch>>​ high ​<< white; or  _______>>​​ molded stone, floor-mounted, with one-inch-wide shoulders,​<< vinyl bumper guard,; or  None - N/A>>​ stainless steel strainer.

Manufacturer: Fiat, Model ​<< MSB-3624; or  MSB-2424>>​.

Trim: <<ASME A112.18.1>>​ exposed wall-type supply with cross handles, spout wall brace, vacuum breaker, hose-end spout, strainers, integral screwdriver stops with covering caps and adjustable threaded wall flanges.

Manufacturer: Fiat, Model 830-AA.

Accessories

5 feet of 1/2 inch diameter plain end reinforced rubber hose, and bracket.

Manufacturer: Fiat, Model 832-AA.

Mop hanger, Manufacturer: Fiat, Model 889-CC.

EMERGENCY SHOWER

      - ***************************************************************************************

      - Refer to LANL Mechanical Standard Detail ST-D2010-1 for emergency equipment details. The following are example specifications for emergency equipment. Edit accordingly to suit project. Consult with manufacturer when equipment requires freeze, corrosion or UV protection. Refer to manufacturers installation details for piping tie-in details.

      - ***************************************************************************************

<<ANSI Z358.1>>; << wall-mounted; or  free standing>>, self cleaning, non-clogging 8 inch diameter << stainless steel; or  plastic>> drench shower head with elbow, << 1 inch; or  1-1/4 inch>>​ IPS supply, instant action stay open valve actuated by rigid stainless steel pull rod. Furnish universal emergency sign.

Manufacturer: Haws, 8100 Series.

EMERGENCY EYE AND FACE WASH

<<ANSI Z358.1>>; << wall-mounted; or  pedestal mounted>>, << stainless steel bowl; or  plastic bowl>>, << 1 inch; or  1-1/4 inch>> IPS supply, instant action stay open valve actuated by << push flag;  foot pedal; or  push flag or foot pedal>>, twin spray heads with << face spray ring;  dust cover assembly; and  wall mount bracket>>, and tailpiece and chrome-plated brass P-trap. Furnish universal emergency sign.

Manufacturer: Haws, ​<< 7000 Series (plastic bowl); or  7300 Series (stainless steel bowl)>>​.

EMERGENCY COMBINATION SHOWER WITH EYE AND FACE WASH

Shower: <<ANSI Z358.1>>​; free standing, self-cleaning, non-clogging, 8-inch-diameter << stainless steel; or  plastic>> drench shower head, instant action stay open valve actuated by rigid stainless steel pull rod.

Eyewash: <<ANSI Z358.1>>; << stainless steel; or  plastic>> bowl with elbow, instant action stay open valve actuated by << push flag;  foot pedal; or  push flag or foot pedal>>, twin spray heads << with face spray ring; and  dust cover assembly>>.

Supply and Waste Piping: 1-1/4 inch IPS.

Furnish universal emergency sign.

      - ***************************************************************************************

      - The following is a designer choice.

      - ***************************************************************************************

Furnish corrosion-resistant coating.

Manufacturer: Haws, 8300 Series.

      - ***************************************************************************************

      - Specify tepid water blending system for use with emergency shower, eye and face wash, and combination stations, as applicable.

      - ***************************************************************************************

TEPID WATER BLENDING SYSTEM

Product Description: Provide an assembly with two backup valves, separate high temperature sensing shut-off valve, separate full-flow pressure relief bypass, and temperature and pressure-compensating blending valve to plus or minus 3 degrees F. Water delivery temperature range 60 to 90 degrees F per <<ANSI Z358.1>>, Appendix B, over a range of flows to 35 gpm.

Manufacturer: HAWS, TWBS.SHE.

PART 3 - EXECUTION

EXAMINATION

Verify walls and floor finishes are prepared and ready for installation of fixtures.

Verify electric power is available and of correct characteristics.

Confirm millwork is constructed with adequate provision for installation of counter top lavatories and sinks.

PREPARATION

Rough-in fixture piping connections in accordance with minimum sizes indicated in fixture rough-in schedule for particular fixtures.

Review millwork shop-drawings. Confirm location and size of fixtures and openings before rough in and installation.

Verify installation of wall supports and/or wall carriers for plumbing fixtures.

INSTALLATION

Install each fixture with trap, easily removable for servicing and cleaning.

Install fixture supplies with smooth bends and no kinks.

Install components level and plumb.

Install and secure fixtures in place with bolts.

Install plumbing fixtures at mounting heights and locations for the handicapped/elderly in accordance with <<ABA Standards>>.

Seal fixtures to wall and floor surfaces with sealant as specified in Section << 07 9200 - Joint Sealants>>​, color to match fixture.

Solidly attach water closets with lag screws. Lead flashing is not intended to hold fixture in place.

Provide chrome plated rigid or flexible supplies to fixtures with stops, reducers, and escutcheons.

      - ***************************************************************************************

      - The following paragraph is a designer choice based on project-specific conditions.

      - ***************************************************************************************

For water closets, install manual flush valve with handle to wide side of stall.

ADJUSTING

Adjust stops or valves for intended water flow rate to fixtures without splashing, noise, or overflow.

CLEANING

Clean plumbing fixtures and equipment.

PROTECTION

Do not permit use of fixtures before final acceptance.

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 22 4200, REV. 8, DATED APRIL 15, 2026.