Section 23 1123 
Facility Natural-Gas Piping

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 7 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Pressure Safety/Mechanical POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable sections from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects. For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality sections.

      - This section is applicable to natural gas systems from the exit of the service meter assembly (or, where no meter is provided, the outlet of the service regulator or service shutoff valve). Items before and including the low-pressure service regulator station are to be installed per Section ​​<< 33 5100 - Natural Gas Distribution>>​​.

  - *************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

      - ***************************************************************************************

      - The following paragraphs are designer choices based on project-specific requirements.

      - ***************************************************************************************

Steel Piping, Above Grade

Plug Valves, Above Grade

Isolation Valves, Above Grade

Test Plug

      - ***************************************************************************************

      - The following Sections are not referenced in the body of this Section. Including them are a designer choice.

      - Section << 01 4000 - Quality Requirements - Non-Nuclear>>

      - Section << 01 4115 - Pressure Safety Submittals>>

      - Section << 01 4216 - Definitions>>

      - Section << 01 8113.13 - Sustainable Design>>

      - ***************************************************************************************

RELATED REQUIREMENTS

Section << 01 2500 - Substitution Procedures>>.

Section << 01 3300 - Submittal Procedures>>.

Section << 01 4000 - Quality Requirements - Non-Nuclear>>.

Section << 01 4115 - Pressure Safety Submittals>>.

Section << 01 4216 - Definitions>>.

Section << 01 4444 - Offsite Welding, Brazing and Joining Requirements>>.

Section << 01 4455 - Onsite Welding, Brazing and Joining Requirements>>.

Section << 01 4525 - Non-Destructive Examination (NDE) Requirements>>.

Section << 01 8113.13 - Sustainable Design>>.

Section << 07 8400 - Firestopping>>.

Section << 09 9100 - Painting>>.

Section << 22 0529 - Hangers and Supports for Plumbing Piping and Equipment>>.

Section << 22 0554 - Identification for Plumbing,  HVAC, and Fire Piping and Equipment>>.

Section << 22 0813 - Testing Piping Systems>>.​

REFERENCE STANDARDS

ASME B16.3 - Malleable Iron Threaded Fittings: Classes 150 and 300.

ASME B16.5 - Pipe Flanges and Flanged Fittings:  NPS 1/2 Through NPS 24 Metric/Inch Standard.

ASME B16.9 - Factory-Made Wrought Buttwelding Fittings.

ASME BPVC-IX - Boiler and Pressure Vessel Code, Section IX - Qualification Standard for Welding, Brazing, and Fusing Procedures; Welders; Brazers; and Welding, Brazing, and Fusing Operators.

ASTM A53/A53M - Standard Specification for Pipe, Steel, Black and Hot-Dipped, Zinc-Coated, Welded and Seamless.

ASTM A197/A197M - Standard Specification for Cupola Malleable Iron.

ASTM A234/A234M - Standard Specification for Piping Fittings of Wrought Carbon Steel and Alloy Steel for Moderate and High Temperature Service.

MSS SP-110 - Ball Valves Threaded, Socket-Welding, Solder Joint, Grooved and Flared Ends.

NFPA 54 - National Fuel Gas Code.

ACTION SUBMITTALS

Submit the following in accordance with Section << 01 3300 - Submittal Procedures>>:

Catalog data on pipe materials, pipe fittings, valves,​<< pipe coating,; or  None - N/A>>​ and accessories.

        - ******************************************************************************

        - The subparagraph below shall be retained when welded joints are specified by the Designer.

        - For high-risk applications such as ML-1 or ML-2, add submittals for "Weld Filler Material Control Procedures" and "Filler Material Certified Material Test Reports (CMTRs)" when required. Add "Post-Weld Heat Treatment Procedures" when required.

        - ******************************************************************************

Per the requirements of << Section 01 4444 - Offsite Welding, Brazing and Joining Requirements; and  Section 01 4455 - Onsite Welding, Brazing and Joining Requirements>>, submit to this section:

          - *******Note: Only required as a submittal for Onsite welding, when subcontractor not using LANL WPS/PQR*******

Welding Procedure Specification (WPS) and supporting Procedure Qualification Record (PQR).

          - ********Note: Only required as a submittal for Onsite welding, when subcontractor not tested at LANL*******

Welder Performance Qualification Records (WPQR) including continuity.

Per the requirements of Section << 01 4525 - Non-Destructive Examination (NDE) Requirements>>, submit to this section:

Written Practice or Procedure for Qualification and Certification of NDE Personnel

NDE Personnel Qualification Records

NDE Procedures

NDE Procedure Qualification Records

NDE Report(s).

QUALITY ASSURANCE

      - ***************************************************************************************

      - Retain the following when steel pipe welding is specified in the Project.

      - ***************************************************************************************

Welders Certification and Qualified Procedure Standards

Interior Steel Pipe:  <<ASME BPVC-IX>> .

Perform work per <<NFPA 54>>.

PART 2 - PRODUCTS

PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section << 01 2500 - Substitution Procedures>>.

      - ***************************************************************************************

      - The following PART 2 Articles are designer choices based on project-specific requirements.

      - ***************************************************************************************

STEEL PIPING, ABOVE GRADE

Pipe: Standard wall, black steel, <<ASTM A53/A53M>>, Type << E; or  S>>, Grade B.  Welded for pipe sizes above 2 inches, threaded for pipe sizes 2 inches or less.

Pipe Fittings: Standard wall

For pipes 2 inch and smaller:  Malleable iron threaded type, <<ASME B16.3>>, <<ASTM A197/A197M>>.

For pipes greater than 2 inches:  Factory made wrought steel butt welding type, <<ASME B16.9>>,  <<ASTM A234/A234M>>, Grade WPB.

Flanges: Steel, weld neck, class 150, raised face, <<ASME B16.5>>​.

Gasket Material: Neoprene, durometer hardness 50-65.

PLUG VALVES, ABOVE GRADE

Valve: Iron body, Female Iron Pipe (FIP) threaded ends or flanged ends to suit piping, plug style, flat head wrench operated, 100 psig working pressure.

Isolation Valves, Above grade

Manufacturer​/Model: NIBCO T-560-CS-R-25-FS-LL

Valve: Carbon steel, female threaded ends or flanged ends to suit piping, reduced port, blowout-proof stem, vented ball, fire safe and maximum rated for 2,000 psig, <<MSS SP-110>>.

TEST PLUG

Size 1/4-inch NPT, brass body, neoprene core, rated for 1,000 psig, complete with sealing cap and gasket, to receive 1/8-inch O.D. probe.

Manufacturer: Pete’s Plug or equivalent.

PART 3 - EXECUTION

INSTALLATION

Furnish and install gas piping per <<NFPA 54>> as applicable.

Do not run gas piping below buildings, structures, or in crawl spaces.  Gas piping installed on the roof shall be elevated above the roof surface and supported.

Do not run gas piping under walks and equipment pads adjacent to building. If this is unavoidable, sleeve line and vent as required.

Install piping to conserve building space and coordinate installation with other trades to optimize the space for all services.  Provide clearance for access to valves and fittings.

Install piping in mechanical rooms parallel to or at right angles to the building walls.

Pressure test piping in accordance with Section << 22 0813 - Testing Piping Systems>>​, for the pressures and durations listed below:

        - ******************************************************************************

        - The following subparagraphs are a designer choice based on project-specific conditions.

        - ******************************************************************************

Operating Pressure up to 14 inches water column (w.c.): Test with inert gas at 10 psig for ​<< 15; or  _______>>​ minutes.

Operating pressure higher than 14 inches w.c.: Test with inert gas at a minimum of 60 psig for << 30; or  _______>>​​ minutes.

Label piping in accordance with Section << 22 0554 - Identification for Plumbing,  HVAC, and Fire Piping and Equipment>>.

      - ***************************************************************************************

      - The following is a designer choice.

      - ***************************************************************************************

Paint outside gas regulator piping, valves, and appurtenances above ground to match building exterior.  Refer to Section << 09 9100 - Painting>>​.

Support piping in accordance with Section << 22 0529 - Hangers and Supports for Plumbing Piping and Equipment>>.

Use threaded joints for above grade piping 2 inches and smaller and butt-welded joints for piping above 2 inches.

Sleeve and caulk pipes penetrating exterior walls or interior bearing walls. Provide waterproof installation for exterior walls. Provide UL/FM approved through-penetration firestop system when penetrating fire-rated barriers (e.g., walls, floors, etc.). See Section << 07 8400 - Firestopping>>​.

Natural Gas pipe purging requirements

Purged fuel gases shall be directly vented to a safe location outdoors, away from personnel and ignition sources.  This may be accomplished through permanent piping or temporary piping or hosing.

If it is not possible to vent purged gases outdoors, the following conditions must be met

Purging activity must be approved by the LANL Fire Marshal based on a documented justification detailing why outdoor venting is not possible and Integrated Work Document (IWD).

Gas concentration in the space to which the purge is vented shall be maintained at no more than 25 percent of the Lower Explosive Limit (LEL). For natural gas, the LEL is a concentration of 5 percent in air or 50,000 ppm. Therefore, a maximum concentration of 12,500 ppm is allowed for natural gas. The concentration may be controlled by providing adequate ventilation or by limiting the amount of purge gas.

Combustible gas detectors shall be used during the purging operation to monitor the gas concentration.

Non-essential personnel shall be evacuated from the vicinity (including adjacent spaces) during the purging operation.

Ignition sources in the purging space shall be controlled or eliminated.

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - *********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 23 1123, REV. 7, DATED APRIL 15, 2026.