Section 23 4133.13 
HEPA Filters – ASME AG-1, Section FC

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 1 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Mechanical POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable Sections from all Divisions, especially Division 1, General Requirements.

      - This template was prepared by an organization operating under a quality assurance program that meets the requirements of 10 CFR 830 (suitable for ML-1 through ML-4 usage).  Implementation of this document requires modification to meet project-specific requirements; responsibility for this lies with the author.  The author shall apply a graded approach to quality assurance based on the management level designation of the project.  When this document is used with nuclear facilities subject to 10 CFR 830, modification to it must be performed by an individual or organization operating under a quality assurance program that meets the requirements of that CFR.

      - ==========================================================

      - This section covers ASME AG-1, Section FC HEPA Filters that are used in the majority of facility ventilation systems at LANL.  These filters include the common sizes of square filters ranging in size from 8” x 8” x 3-1/16” (with a flow rate of 25 scfm) up to 24” x 24” x 11-1/2” (with a flow rate of 2000 scfm).  Two other types of HEPA filters are covered in two other sections:

        - Section ​​<< 23 4133.16 - HEPA Filters - ASME AG-1, Section FK, Special>>​​ includes radial-flow filters, axial-flow circular filters, and axial-flow rectangular filters that are not included in Section FC.

        - Section ​​<< 23 4133.19 - HEPA Filters – Auxiliary Nuclear Grade>>​​ includes encapsulated filters with one or two end connections and other filter configurations not included in ASME AG-1, Sections FC or FK.

      - Higher pressure, high efficiency filters for process piping (e.g., Swagelok) are addressed in Section ​​<< 43 3113.37 - High Efficiency Gas Purification Filters>>​​.

      - The filters listed in the Specifier’s Reference webposted under Section ​​<< 23 4133.13 - HEPA Filters – ASME AG-1, Section FC>>​​​ in LANL Engineering Standards Specification Website are all HEPA filters that have been qualified to Article 5000 of ASME AG-1, Section FC. These filters shall be specified where available and practical.

  - *************************************************************************************************************

PART 1 - general

Section Includes

<<ASME AG-1>>, Section FC HEPA Filters

      - ***************************************************************************************

      - Retain Related Sections as applicable. If none are applicable, retain "None."

      - ***************************************************************************************

Related requirements

None.

Section ​<< 23 3225 - Bag-In Bag-Out Housings>>​.

Section ​​<< 23 4133.16 - HEPA Filters - ASME AG-1, Section FK, Special>>​​.

Section << 23 4133.19 - HEPA Filters – Auxiliary Nuclear Grade>>.

Applicability

Filters to be installed in confinement ventilation systems for containing radioactive particles; their safety function and primary critical characteristic is particle removal efficiency of at least 99.97 percent for 0.3 micrometer particles of an approved aerosol test.

Procurement and installation of HEPA filters for Department of Energy (DOE) facilities at Los Alamos National Laboratory (LANL).

Filters for use in air and gas streams with a 250 degrees F maximum continuous temperature.

    - **********************************************************************************************

      - Except for ASME NQA-1 (2008 with 2009 Addenda is required), follow latest edition of all documents invoked herein (editions below reflect those used in the development of this template).

      - The codes/standards listed below are provided for reference only and are not listed within the body of this section. It is a user-choice to include these codes/standards.

      - <<10 CFR 830.122>>

      - The edition of QPA-RIT-WI-002 Attachments 1 through 3 need to be verified as latest; if it is revised, then the following reference AND Appendix A will need review for revision by specifier (and notify Section POC) https://int.lanl.gov/org/ddops/aldbus/si/dcrm/dcrm-docs/IQPA/QPA-RIT-WI-002.pdf  (LANL only)

    - **********************************************************************************************

REFERENCE STANDARDS

10 CFR 830.122 - Nuclear Safety Management, Quality Assurance Criteria.

40 CFR 261 - Identification and Listing of Hazardous Waste.

ASME AG-1 - Code on Nuclear Air and Gas Treatment.

ASME NQA-1 - Quality Assurance Requirements for Nuclear Facility Applications.

DOE-HDBK-1169 - Nuclear Air Cleaning Handbook.

DOE-STD-3020 - Specification for HEPA Filters Used by DOE Contractors.

UL 586 - High Efficiency, Particulate, Air Filter Units.

Los Alamos National Laboratory QPA-RIT-WI-002, Receipt Inspection of ML-1, ML-2, and ML-3 HEPA Filters Used in Ventilation Systems

Definitions

For definitions and acronyms, refer to COE Glossary of Terms.

Acceptance Test: Inspection and testing of a filter to verify certain characteristics or properties, which determine the acceptance or rejection of that filter.

Air Flow:  The volume of air through a system per unit of time, expressed as standard cubic feet per minute (scfm) or actual cubic feet per minute (acfm).

Approved Test Aerosol: Particle-generating materials approved by DOE and used as test aerosols for performing testing of HEPA filters.

<<ASME AG-1>>, Section FC HEPA Filters: Axial-flow, square, open-faced, fire-resistant HEPA filters used in nuclear air cleaning systems.

C of C: Certificate of Conformance:  Defined under “Action Submittals” article.

DOE:  Department of Energy.

EPA: Environmental Protection Agency.

Filter Test Facility (FTF): A facility established by the DOE specifically to conduct performance tests and quality assurance inspections of HEPA filters.

High Efficiency Particulate Air (HEPA) Filter: A throwaway, extended-medium dry-type filter with a rigid casing enclosing the full depth of the pleats. The filter shall exhibit a minimum efficiency of 99.97 percent when tested with an aerosol of 0.3 µm diameter.

In-Place Leakage Test:  A test conducted after HEPA filters have been installed where the downstream test aerosol concentration (in µg/liter) is compared to the upstream test aerosol concentration (in µg/liter) and is reported as a percentage. This test uses a polydispersed aerosol having a light-scattering number mean diameter of 0.7 µm and a size range of 0.1 to 3.0 µm.

LANL: Los Alamos National Laboratory.

Nominal Air Flow Rating: The flow rate which HEPA filters are identified by the manufacturer and confirmed at the FTF.

Nuclear Facility: A DOE facility in which radioactive materials are produced or handled to the degree that environmental protection is required.

Penetration: The downstream test aerosol concentration, expressed as a percentage of the upstream test aerosol concentration where a monodispersed aerosol with a light-scattering number mean diameter of 0.3 µm is used.

QA: Quality Assurance.

Qualification Test: A test, often destructive, of a prototype or randomly selected production filter to establish its capability to meet certain functional and specification requirements.  The results of the test are considered to be typical of individual items or model number, which are of the same design and are manufactured by the same process.

SST: Stainless steel.

w.g.:  water gage.

LANL-PERFORMED WORK

LANL will perform receipt inspection on filters ordered by LANL organizations in accordance with Article ​<< 3.1; or  ______>>​ Examination of this Section.

LANL will perform in-place leakage testing of HEPA filter(s) after successful installation in systems required to be tested.

ACTION Submittals

      - ***************************************************************************************

      - Submittal of QA plan is not necessary if filter manufacturer is on the current LANL Institutional Evaluated Suppliers List (IESL)  (LANL access only).

      - The Submittals as listed are required for ML-1, ML-2, and ML-3 HEPA filters.  For ML-4 HEPA filters, the Submittals listed may be edited to include fewer requirements.

      - For Safety Class (ML-1) and Safety Significant (ML-2) applications the filters must be qualified to ASME AG-1, Section FC.

      - ***************************************************************************************

From Manufacturer before order placement

Certification documentation from an independent test facility indicating that HEPA filter model(s) have been successfully qualified or requalified within the past five years in accordance with <<ASME AG-1>>, Article FC-5100 (with <<DOE-STD-3020>>, Section 6.1.2 allowances).

From Manufacturer before shipment

Certified performance test results by the manufacturer for aerosol penetration and airflow resistance. Test results shall be identified for each filter by serial number.

Copy of the HEPA filter manufacturer’s QA plan identifying procurement, fabrication, test & inspection, material traceability and non-conformity controls for approval.

Certificate of Conformance (C of C) that is signed or otherwise authenticated by authorized individuals certifying the degree to which items or services meet specified requirements. (Paraphrased from <<ASME AG-1>>, Article AA-1400). The C of C shall include:

Purchase Order (PO) number.

Purchased item identified by model number.

The serial numbers of all filters included in the shipment to which the C of C is applicable.

Any approved changes, waivers, or deviations from this Section.

Statement indicating that filters meet the following requirements

The filters conform to the requirements in <<ASME AG-1>>, Section FC; manufacturer’s QA plan; and Article ​​​<< 1.8; or  ___>>​​​, Quality Assurance, of this Section.

Filter construction and dimensions are per  <<DOE-STD-3020>> and Article ​​<< 2.3; or  ___>>​​, Design Requirements of this Section.

Qualification and Acceptance Test reports submitted above are applicable to the items delivered, and (if necessary) cross-referenced by serial number and any other item identifier.

            - *************************************************************

            - The following statement regarding gaskets only applies to elastomer-type gaskets. This statement is to be omitted for gelatinous-seal-style filters.

            - *************************************************************

Gaskets shall be glued firmly and continuously to the case. Gasket shall not extend more than 1/16 in. (1.6 mm) over either side of the seating surface at any point.

            - *************************************************************

            - The following statement regarding case panels only applies to metal case filters.  It is included here to meet guidance in DOE-HDBK-1169 Appendix B.

            - *************************************************************

Case panels have been assembled into the frame by potting a sub-assembly consisting of the filter pack and side panels into the top and bottom panels (but not corners) using adhesive meeting the requirements of <<DOE-STD-3020>>.

Certification of compliance with <<UL 586>>, and appropriate label applied to filter case, as evidence of compliance with requirements for resistance to flame and heated air.

Warranty documentation – guarantee against failure in proper use or operation caused by defective materials and/or workmanship for a period of one year from the date of acceptance at LANL.

From FTF before shipment

Certified performance test results by the FTF for aerosol penetration and airflow resistance.  Test results identified for each filter by serial number.

quality assurance

Seller’s Quality Assurance Requirements

Manufacture, inspect, test, and ship filters under a quality assurance program meeting the applicable requirements of <<ASME NQA-1>> -2008 with 2009 addenda.

Packaging and shipping

Package and ship filters in accordance with  <<ASME AG-1>>,  Article FC-7000,  <<DOE-STD-3020>> (Sections 7.2 and 7.3), and:

Place filter cartons in a sturdy wooden crate with the lid/top secured with removable screws or lag bolts to eliminate unit handling at carrier interchange points and avoid unnecessary damage. Label crates per <<ASME AG-1>>,  Article FC-9200.

Ship filters properly oriented, as indicated on shipping container.

For large shipments, ship the entire shipment in a sealed, dedicated trailer to provide an additional quality assurance of product shipping and handling.

Filters returned to the manufacturer from the FTF or shipped from the FTF to LANL shall be re-packaged per the above requirements.

PART 2 - products

manufacturers

The following is a list of some of the manufacturers with qualified nuclear grade HEPA filter products that may meet the requirements of this Section and <<ASME AG-1>>, Section FC; however, these manufacturers are not exempt from any seller requirements​​<< including the submission of qualification certification for approval; or  None - N/A>>​​ .

AAF International (American Air Filter).

AAF| Flanders.

Camfil Inc.

product options and substitutions

No substitutions allowed.

DESIGN REQUIREMENTS

Materials for the components below are specified in Article ​​​​​<< 2.4; or  ___>>​​​​​, Materials of Construction.

        - ******************************************************************************

        - Edit Design Requirements as necessary for specific application.

        - Type and number designation as defined in ASME AG-1, Section FC:

        - •     Type A – Folded filter media with corrugated separator/supports

        - •     Type B – Mini pleat filter medium with glass ribbon or self-       extinguishing thread separators

        - •     Type C – Continuous corrugated filter media folded without        separator

        - •     Type D – Folded filter media with glass or self-extinguishing        thread separators

        - •     Number Designation:

          - 1 – size: 8 in. x 8 in. x 3 1/16 in., min. rated air flow: 25 scfm, at 1.3 in. w.g. (max.)

          - 2 – size: 8 in. x 8 in. x 5 7/8 in., min. rated air flow: 50 scfm, at 1.3 in. w.g. (max.)

          - 3 – size: 12 in. x 12 in. x 5 7/8 in., min. rated air flow: 125 scfm, at 1.3 in. w.g. (max.)

          - 4 – size: 24 in. x 24 in. x 5 7/8 in., min. rated air flow: 500 scfm, at 1.0 in. w.g. (max.)

          - 5 – size: 24 in. x 24 in. x 11 1/2 in., min. rated air flow: 1000 scfm, at 1.0 in. w.g. (max.)

          - 6 – size: 24 in. x 24 in. x 11 1/2 in., min. rated air flow: 1250 scfm, at 1.3 in. w.g. (max.)

          - 7 – size: 24 in.  x 24 in. x 11 1/2 in., min. rated air flow: 1500 scfm, at 1.3 in. w.g. (max.)

            - Specifier: While the 2000 scfm filter is listed below, there is currently debate as to its loading characteristics.  It is recommended that this filter not be selected without careful review of expected filter change-out frequency.

          - 8 – size: 24 in. x 24 in. x 11 1/2 in., min. rated air flow: 2000 scfm, at 1.3 in. w.g. (max.)

          - 9 – size: 12 in. x12 in. x11 1/2 in., min. rated air flow: 250 scfm, at 1.3 in. w.g. (max.)

        - ******************************************************************************

Design in accordance to <<ASME AG-1>>, Article FC-4000, Design.

Type ​​​​<< A;  B;  C; or  D>>​​​​ Filter Pack.

Number Designation ​​<< ***Include the Number Designation and the flow rate and associated pressure drop. Example: 7, 1500 scfm @ 1.3” w.g.***>>​​  per <<ASME AG-1>>, Table FC-4110.

Case Type: ​​​<< Wood;  Metal; or  Wood or Metal>>​​​.

        - ******************************************************************************

        - The type of gasket to be specified depends on the type of sealing mechanism that is used to seal the filter to the mounting surface.  Neoprene, epichlorohydrin, and silicone gaskets are all used for a flat sealing surface.  Gelatinous seal gaskets are used for a knife edge sealing surface.  Neoprene gaskets are used on qualified HEPA filters manufactured by AAF and AAF|Flanders. Epichlorohydrin gaskets are used on qualified HEPA filters manufactured by Camfil.  Silicone gaskets are used on high temperature qualified HEPA filters manufactured by AAF and AAF|Flanders.  Silicone gaskets should only be specified for high-temperature filters.  (High-temperature filters are mainly used in the facility systems at TA-55.)

        - The following two subparagraphs are a designer choice.

        - ******************************************************************************

Gasket Type and Location: ​​<< Elastomer Seal; or  Gelatinous Seal>>​​ on ​​<< Upstream Face;  Downstream Face; or  Both Faces>>​​.

Faceguard: ​​<< Galvanized steel; or  Stainless Steel>>​​ on both faces.

        - ******************************************************************************

        - Separators are only specified for Type A Filter Packs.  Separators used for Type A Filter Packs are made from aluminum.  If aluminum could be corroded by the airstream to which the filter will be exposed, then Coated (vinyl coating) should be specified.

        - ******************************************************************************

Separators (for Type A Filter Packs only): ​​<< Coated; or  Uncoated>>​​ Aluminum.

Materials of construction

General

The following are unacceptable materials of construction: particle board, asbestos, cadmium-coated metals, and any material that generates EPA regulated wastes as specified in <<40 CFR 261>>.

Filter Media

Manufacture silicate media in accordance with <<ASME AG-1>>, Article FC-3130.

Case

        - ******************************************************************************

        - Before specifying wood-case filters, verify that they are still allowed under the current combustible load analysis for the facility.  Facilities with large filter plenums may now be restricting the use of wood-case HEPA filters.  Note:  Wood-case filters generally cost less than metal-case filters but are more likely to be rejected during receipt inspection due to being out of square. Also, metal-case filters weigh approximately 50% more than wood-case filters, so ensure mounting frames can support the additional weight.

        - ******************************************************************************

Stainless Steel, Type ​<< 304; or  316>>​ in accordance with <<ASME AG-1>>, Article FC-3110 (a).

Plywood, in accordance with <<ASME AG-1>>, Article FC-3110 (b).

Fasteners

Use fasteners that are in accordance with (Section 5.3.7).

      - ***************************************************************************************

      - Select only one type of separator per filter. Type C filters are the only filter that do not use separators. All of the filters listed in the Specifier’s Reference webposted under Section ​<< 23 4133.13 - HEPA Filters – ASME AG-1, Section FC>>​ in LANL Engineering Standards Specification Website—except for Number Designation 8 filters—use aluminum separators, coated aluminum separators, or use separatorless filter media. Number Designation 8 filters use string separators.

      - ***************************************************************************************

Separators (when used)

Aluminum, conforming to <<ASME AG-1>>, Article FC-3160, (a).

Acid-Resistant Aluminum, conforming to <<ASME AG-1>>, Article FC-3160, (b).

Glass Ribbon, conforming to <<ASME AG-1>>, Article FC-3160, (c).

String, conforming to <<ASME AG-1>>, Article FC-3160, (d).

      - ***************************************************************************************

      - The high-temperature-resistant RTV silicone is only specified for High Temperature filters.  These filters have mainly been used in TA-55 facility systems.

      - ***************************************************************************************

Adhesives used to fasten gaskets to filter case, and seal the filter pack or faceguards to the case.

Self-extinguishing in accordance with the spot-flame test of  <<ASME AG-1>>, Article FC-5160 or <<UL 586>>.

High-temperature-resistant, red RTV silicone.

Gaskets and Seals

        - ******************************************************************************

        - Retain only one of the two following subparagraphs.

        - ******************************************************************************

Elastomer Gasket – in accordance with <<DOE-STD-3020>> (Section 5.3.5.1).

        - *** OR ***

Gelatinous Seal – in accordance with <<DOE-STD-3020>>​ (Section 5.3.5.2).

Faceguards

        - ******************************************************************************

        - Specify Type 304 stainless steel for highly-corrosive atmospheres.

        - ******************************************************************************

Faceguards – galvanized steel in accordance with <<ASME AG-1>>, Article FC-3140.

Faceguards –Type 304 stainless steel in accordance with <<ASME AG-1>>, Article FC-3140.

Fabrication

General

Fabricate in accordance with <<ASME AG-1>>, Article FC-6000;  <<DOE-STD-3020>> (Section 5.4 including Table 5-2); and  <<ASME NQA-1>> -2008 with 2009 addenda.

        - ******************************************************************************

        - The following two subparagraphs are designer choices.

        - ******************************************************************************

Separator filters shall comply with <<ASME AG-1>>, Article FC-4130.

Separator-less filters shall comply with <<DOE-STD-3020>> (Section 5.4.2).

Install faceguards in each face of all filters in accordance with <<ASME AG-1>>, Article FC-4160.

        - ******************************************************************************

        - The following two subparagraphs are designer choices.

        - ******************************************************************************

Install elastomer gasket on ​​<< upstream;  downstream; or  both>>​​ face(s of filter in accordance with <<ASME AG-1>> (Article FC-4141) and <<DOE-STD-3020>> (Section 5.4.4).

Install gelatinous seal on ​<< upstream; or  downstream>>​ face of filter in accordance with <<ASME AG-1>>, Article FC-4142. ​<< Install extraction clips on the opposite face of the case from where the gelatinous seal is located.; or  None - N/A>>​

        - ******************************************************************************

        - The labeling includes a UL label indicating successful testing per UL 586. The UL label is required for all qualified HEPA filters.

        - Leave in the statement "The specific application for these filters allows the label to be applied directly to the filter case" when specifying High Temperature filters. Normal business practice for some of the filter manufacturers is to only loosely attach the labels using tape or not attaching the labels to the filter at all, just leaving them loose in the carton. The normal business practice is not acceptable for ML-1 and ML-2 applications.

        - ******************************************************************************

Label each filter and shipping container (carton containing one filter) in accordance with <<DOE-STD-3020>> (Section 6.1.6). Labels must be permanently affixed to the filter. ​<< The specific application for these filters allows the label to be applied directly to the filter case.; or  None - N/A>>​

Acceptance testing

Qualification and Acceptance Test Criteria

        - ******************************************************************************

        - Safety Class (ML-1) and Safety Significant (ML-2) applications require that a qualified filter be specified. Make every effort to select a qualified filter from the Specifier’s Reference webposted under Section ​<< 23 4133.13 - HEPA Filters – ASME AG-1, Section FC>>​ in ​LANL Engineering Standards Specification Website.

        - ******************************************************************************

Have qualification testing of filters and filter media performed by an independent test facility in accordance with <<ASME AG-1>>, Article FC-5100 (with <<DOE-STD-3020>>, Section 6.1.2 allowances) prior to start of manufacturing of filters for this purchase.

Perform factory inspection of filters in accordance with <<ASME AG-1>>, Article FC-5200. Additionally, LANL will be inspecting the filters to LANL QPA-RIT-WI-002.007 (see Appendix A, Table 2 for inspection criteria). Filters that do not meet these inspection criteria will be rejected.

Perform factory production testing of aerosol penetration and resistance to air flow for each filter in accordance with <<ASME AG-1>>, Article FC-5300.

Ship filters to the FTF (Air Techniques International Testing Laboratories, Suite 104, 1708 Whitehead Rd., Baltimore, MD 21207, phone 410-277-8981, fax 410-277-3448, email ATITL@atitest.com) to have inspection and performance acceptance testing performed in accordance with <<ASME AG-1>>, Article FC-5300, <<DOE-STD-3020>> and LANL QPA-RIT-WI-002.007, Table 2 (see Appendix A). Filters that do not meet these inspection criteria are not acceptable.

PART 3 - execution (performed by AND AT lanl)

Examination

Inspect all filters upon shipment receipt to LANL QPA-RIT-WI-002.007. Verify documentation from Article ​​​​​<< 1.7; or  ___>>​​​​​, Action Submittals, is included and is complete.

Storage

Store filters in accordance with <<ASME AG-1>>, Article FC-7000, <<DOE-HDBK-1169>>, Appendix A or the manufacturer’s requirements, whichever is more restrictive; also:

Store filters properly oriented, as indicated on shipping container.

When stored out of the shipping container, stagger the box pattern on each level so as to not have columns of boxes that can easily topple.

Shelf life: Do not store filters for more than 10 years after manufacture date.

Handling and installation

Handle and install HEPA filters in accordance with Appendix A, Parts A.5 and A.6.

Field Quality control

In-place leak test filters after installation per LANL requirements.

Replace all filters that fail LANL in-place leakage test.

Notify Seller, Purchasing Group, and Quality Assurance Group of filter rejections and re-evaluate the future procurement status of that manufacturer and/or model.

      - ***************************************************************************************

      - Appendix A is to be included with all ML-1, ML-2, and ML-3 filter procurements; verify that it is latest at https://int.lanl.gov/org/ddops/aldbus/si/dcrm/dcrm-docs/IQPA/QPA-RIT-WI-002.pdf (LANL only). Update as required.

      - ***************************************************************************************

end of MAIN SECTION; APPENDIX FOLLOWs

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 23 4113.13, REV. 1, DATED APRIL 15, 2026.

END OF SECTION