Section 23 4133.16 
HEPA Filters - ASME AG-1, Section FK, Special

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 1 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Mechanical POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable sections from all Divisions, especially Division 1, General Requirements.

      - This template was prepared by an organization operating under a quality assurance program that meets the requirements of 10 CFR 830 (suitable for ML-1 through ML-4 projects). Implementation of this document requires modification to meet project-specific requirements; responsibility for this lies with the author. The author shall apply a graded approach to quality assurance based on the management level designation of the project. When this document is used with nuclear facilities subject to 10 CFR 830, modification to it must be performed by an individual or organization operating under a quality assurance program that meets the requirements of that CFR.

      - ==========================================================

      - This section covers ASME AG-1, Section FK, Special HEPA filters that include radial-flow filters, axial-flow circular filters, and axial-flow rectangular filters that are not included in Section FC. Two other types of HEPA filter are covered in two other sections:

        - Section ​<< 23 4133.13 - HEPA Filters – ASME AG-1, Section FC>>​ that includes common sizes of square filters with flow rates of up to 2000 scfm.

        - Section ​<< 23 4133.19 - HEPA Filters – Auxiliary Nuclear Grade>>​​includes encapsulated filters with one or two end connections and other filter configurations not included in ASME AG-1, Sections FC or FK.

      - Higher pressure, high efficiency filters for process piping (e.g., Swagelok) are addressed in Section ​<< 43 3113.37 - High Efficiency Gas Purification Filters>>​​.

      - The filters listed in the Specifier’s Reference webposted under Section ​<< 23 4133.13 - HEPA Filters – ASME AG-1, Section FC>>​ in LANL Engineering Standards Specification Website are all HEPA filters that have been qualified to Article 5000 of ASME AG-1, Section FC. These filters can be used as the basis for determining if a Type 2 or Type 4 Section FK filter is eligible to be considered qualified.

  - *************************************************************************************************************

PART 1 - general

Section Includes

<<ASME AG-1>>, Section FK Special HEPA Filters.

      - ***************************************************************************************

      - Retain Related Sections as applicable. If none are applicable, retain "None."

      - ***************************************************************************************

Related requirements

None.

Section ​​​<< 23 3225 - Bag-In Bag-Out Housings>>​​​.

Section ​​<< 23 4133.13 - HEPA Filters – ASME AG-1, Section FC>>​​.

Section << 23 4133.19 - HEPA Filters – Auxiliary Nuclear Grade>>.

Applicability

Filters to be installed in confinement ventilation systems for containing radioactive particles; their safety function and primary critical characteristic is particle removal efficiency of at least 99.97 percent for 0.3 micrometer particles of an approved aerosol test.

Procurement and installation of HEPA filters for Department of Energy (DOE) facilities at Los Alamos National Laboratory.

Filters for use in air and gas streams with a 250 degrees F maximum continuous temperature.

    - **********************************************************************************************

      - Except for ASME NQA-1 (2008 with 2009 Addenda is required), follow latest edition of all documents invoked herein (editions below reflect those used in the development of this template).

      - The codes/standards listed below are provided for reference only and are not listed within the body of this section. It is a user-choice to include these codes/standards.

      - <<10 CFR 830.122>>

      - The edition of QPA-RIT-WI-002 Attachments 1 through 3 need to be verified as latest; if it is revised, then the following reference AND Appendix A will need review for revision by specifier (and notify Section POC) https://int.lanl.gov/org/ddops/aldbus/si/dcrm/dcrm-docs/IQPA/QPA-RIT-WI-002.pdf  (LANL only)

    - **********************************************************************************************

Reference standards

10 CFR 830.122 - Nuclear Safety Management, Quality Assurance Criteria.

40 CFR 261 - 40 CFR 261.

ASME AG-1 - Code on Nuclear Air and Gas Treatment.

ASME NQA-1 - Quality Assurance Requirements for Nuclear Facility Applications.

DOE-HDBK-1169 - Nuclear Air Cleaning Handbook.

DOE-STD-3020 - Specification for HEPA Filters Used by DOE Contractors.

UL 586 - High Efficiency, Particulate, Air Filter Units.

Los Alamos National Laboratory QPA-RIT-WI-002, Receipt Inspection of ML-1, ML-2, and ML-3 HEPA Filters Used in Ventilation Systems

Definitions

For definitions and acronyms, refer to COE Glossary of Terms.

Acceptance Test: Inspection and testing of a filter to verify certain characteristics or properties, which determine the acceptance or rejection of that filter.

Air Flow:  The volume of air through a system per unit of time, expressed as standard cubic feet per minute (scfm) or actual cubic feet per minute (acfm).

Approved Test Aerosol: Particle-generating materials approved by DOE and used as test aerosols for performing testing of HEPA filters.

<<ASME AG-1>>, Section FC HEPA Filters: Axial flow square open faced, fire resistant, HEPA filters used in nuclear air cleaning systems.

<<ASME AG-1>>, Section FK Special HEPA Filters:  Radial flow, Axial flow circular open face, and Axial flow rectangular open face (not covered by Section FC), fire resistant, HEPA filters used in nuclear air cleaning systems.

C of C: Certificate of Conformance: A document signed or otherwise authenticated by an authorized individual certifying the degree to which items or services meet specified requirements.

DOE: Department of Energy.

EPA: Environmental Protection Agency.

Filter Test Facility (FTF): A facility established by the DOE specifically to conduct performance tests and quality assurance inspections of HEPA filters.

High Efficiency Particulate Air (HEPA) Filter:  A throwaway, extended-medium dry-type filter with a rigid casing enclosing the full depth of the pleats.  The filter shall exhibit a minimum efficiency of 99.97 percent when tested with an aerosol of 0.3 µm diameter.

In-Place Leakage Test:  A test conducted after HEPA filters have been installed where the downstream test aerosol concentration (in µg/liter) is compared to the upstream test aerosol concentration (in µg/liter) and is reported as a percentage. This test uses a polydispersed aerosol having a light-scattering number mean diameter of 0.7 µm and a size range of 0.1 to 3.0 µm.

LANL: Los Alamos National Laboratory.

Nominal Air Flow Rating: The flow rate which HEPA filters are identified by the manufacturer and confirmed at the FTF.

Nuclear Facility: A DOE facility in which radioactive materials are produced or handled to the degree that environmental protection is required.

Penetration: The downstream test aerosol concentration, expressed as a percentage of the upstream test aerosol concentration where a monodispersed aerosol with a light-scattering number mean diameter of 0.3 µm is used.

QA: Quality Assurance.

Qualification Test: A test, often destructive, of a prototype or randomly selected production filter to establish its capability to meet certain functional and specification requirements.  The results of the test are considered to be typical of individual items or model number, which are of the same design and are manufactured by the same process.

SST: Stainless steel.

w.g.: water gage.

LANL-PERFORMED WORK

LANL will perform receipt inspection on filters ordered by LANL organizations in accordance with Article << 3.1; or  ______>> Examination of this Section.

LANL will do in-place leakage testing of HEPA filter(s) after successful installation in systems required to be tested.

ACTION Submittals

      - ***************************************************************************************

      - Submittal of QA plan is not necessary if filter manufacturer is on the current LANL Institutional Evaluated Suppliers List (IESL)  (LANL access only).

      - The Submittals as listed are required for ML-1, ML-2, and ML-3 HEPA filters.  For ML-4 HEPA filters, the Submittals listed may be edited to include fewer requirements.

      - For Safety Class (ML-1) and Safety Significant (ML-2) applications the filters must be qualified to ASME AG-1, Section FK.

      - ***************************************************************************************

From Manufacturer before order placement.

        - ******************************************************************************

        - Article FK-5100 is used for qualification testing of Type 1 Radial flow filters.

        - Article FK-5200 is used for qualification testing of Type 2 Axial flow circular filters

        - Article FK-5400 is used for qualification testing of Type 4 Axial flow rectangular filters

        - The following is a designer choice.

        - ******************************************************************************

Certification documentation from an independent test facility indicating that HEPA filter model(s) have been successfully qualified or requalified within the past five years in accordance with <<ASME AG-1>> ASME AG-1, Article << FK-5100;  FK-5200; or  FK-5400>> (with <<DOE-STD-3020>>, Section 6.1.2 allowances).

From Manufacturer before shipment.

Certified performance test results by the manufacturer for aerosol penetration and airflow resistance. Test results are to be identified for each filter by serial number.

Copy of the HEPA filter manufacturer’s QA plan identifying procurement, fabrication, test & inspection, material traceability and non-conformity controls for approval.

Certificate of Conformance (C of C) that is signed or otherwise authenticated by authorized individuals certifying the degree to which items or services meet specified requirements. (Paraphrased from <<ASME AG-1>>, Article AA-1400.). The C of C shall include:

Purchase Order (PO) number.

Purchased item identified by model number.

The serial numbers of all filters included in the shipment to which the C of C is applicable.

Any approved changes, waivers, or deviations from this Section.

Statement indicating that filters meet the following requirements:

The filters conform to the requirements in <<ASME AG-1>>, Section FK, manufacturer’s QA plan, and Article ​​<< 1.8; and  ___>>​​, Quality Assurance, of this Section.

Filter construction is per <<DOE-STD-3020>> and Article ​​<< 2.3; and  ___>>​​, Design Requirements, of this Section.

Qualification and Acceptance Test reports submitted above are applicable to the items delivered, and (if necessary) cross reference by serial number and any other item identifier.

            - *************************************************************

            - The following statement regarding gaskets only applies to elastomer-type gaskets. This statement is to be left inactive for gelatinous-seal-style filters.

            - *************************************************************

Gaskets shall be glued firmly and continuously to the case. Gasket shall not extend more than 1/16 in. (1.6 mm) over either side of the seating surface at any point.

            - *************************************************************

            - The following statement regarding case panels only applies to Type 4 filters with a metal case. It is included here to meet a requirement in DOE-HDBK-1169-2003, Appendix B.

            - *************************************************************

Case panels have been assembled into the frame by potting a sub-assembly consisting of the filter pack and side panels into the top and bottom panels (but not corners) using adhesive meeting the requirements of <<DOE-STD-3020>>.

Certification of compliance with <<UL 586>>, and appropriate label applied to filter case, as evidence of compliance with requirements for resistance to flame and heated air.

Warranty documentation - guarantee against failure in proper use or operation caused by defective materials and/or workmanship for a period of 1 year from the date of acceptance at LANL.

From the FTF before shipment.

Certified performance test results by the FTF for aerosol penetration and airflow resistance. Test results identified for each filter by serial number.

quality assurance

Seller’s Quality Assurance Requirements.

Manufacture, inspect, test, and ship filters under a quality assurance program meeting the applicable requirements of <<ASME NQA-1>>-2008 with 2009 addenda.

Packaging and shipping

Package and ship filters in accordance with <<ASME AG-1>> Article FK-7000; <<DOE-STD-3020>>, Sections 7.2 and 7.3; and:

Place filter cartons in a sturdy wooden crate with the lid/top secured with removable screws or lag bolts to eliminate unit handling at carrier inter change points and avoid unnecessary damage.  Shipping crates shall be labeled in accordance with <<ASME AG-1>> Article FK-9200.

Ship filters properly oriented, as indicated on shipping container.

For large shipments, ship the entire shipment in a sealed dedicated trailer to provide an additional quality assurance of product shipping and handling.

Filters returned to the manufacturer from the FTF or shipped from the FTF to LANL must be re-packaged per the above requirements.

PART 2 - products

manufacturers

The following is a list of some of the manufacturers that produce nuclear grade HEPA filter products that may meet the requirements of this Section and <<ASME AG-1>>, Section FK.  However, these manufacturers are not exempt from any seller requirements ​<< including the submission of qualification certification for approval; or  None - N/A>>​.

AAF International (American Air Filter).

AAF | Flanders.

Camfil Inc.

PRODUCT OPTIONS AND SUBSTITUTIONS

No substitutions allowed.

DESIGN REQUIREMENTS

Materials for the components below are specified in Article ​​​​​<< 2.4; or  ___>>​​​​​, Materials of Construction.

        - ******************************************************************************

        - Edit Design Requirements as necessary for specific application.

        - Type 1:  As of the date of this document, no Section FK Type 1 HEPA filters have been qualified by any of the three manufacturers from which LANL usually buys filters.  Therefore, the use of Type 1 filters is discouraged at this time.

        - Types 2 and 4: Both Type 2 and Type 4 filters may be deemed qualified based on the qualification of a filter size listed in ASME AG-1, Section FC, Table FC-4110-1. The filters listed in the Specifier’s Reference webposted under ​<< 23 4133.13 - HEPA Filters – ASME AG-1, Section FC>>​ in LANL Engineering Standards Specification Website have been qualified to Article 5000 of ASME AG-1, Section FC. These filters can be used as the basis for determining if a Type 2 or Type 4 Section FK filter is eligible to be considered qualified. See ASME AG-1, Section FK, Articles FK-5200 and FK-5400; and DOE-STD-3020-2015 (Section 6.1.2) for guidance on determining how to use the information contained in the Specifier’s Reference. Types of HEPA Filter as defined in ASME AG-1, Section FK

        - •     Type 1 – Radial flow filters

        - •     Type 2 – Axial flow circular filters

        - •     Type 4 – Axial flow rectangular filters that are size variation of       those addressed in ASME AG-1, Section FC

        - Types of Filter Pack are defined in ASME AG-1, Section FK

        - •     Type A – Folded filter media with corrugated separator/supports

        - •     Type B – Mini-pleat medium with glass fiber or noncombustible thread separators

        - •     Type C – Continuous corrugated filter media folded without separators

        - •     Type D – Folded filter media with glass fiber ribbon separators of glass fiber media or noncombustible threads glued to filter media

        - ******************************************************************************

Design in accordance to <<ASME AG-1>>, Article FK-4000, Design.

Type ​​​​<< 1;  2; or  4>>​​​​ HEPA filter.

Type ​​​<< A;  B;  C; or  D>>​​​ Filter Pack (A and B only apply to Type 2 and 4 HEPA filters).

Case Material: ​​​<< Wood (for Type 4 only); or  Metal>>​​​.

Gasket Type and Location: ​​​<< Elastomer Seal; or  Gelatinous Seal>>​​​ on ​​​<< Internal or External (for Type 1 HEPA filter only); or  Upstream Face, Downstream Face, or Both Faces (for Types 2 and 4 HEPA filters only)>>​​​.

        - ******************************************************************************

        - The following two subparagraphs are designer choices.

        - ******************************************************************************

Faceguard: ​​​​​<< Galvanized steel; or  Stainless steel>>​​​​​ on both faces (for Types 2 and 4 HEPA filters only).

Grilles: ​​​​<< Stainless steel;  Perforated metal; or  Expanded metal>>​​​​ (for Type 1 HEPA filters only).

        - ******************************************************************************

        - Separators are only specified for Type A Filter Packs. Separators used for Type A Filter Packs are made from aluminum.  If aluminum will be corroded by the airstream the filter will be exposed to then a coated separator (vinyl coating) should be specified.  Type B and D filter packs have glass fiber or noncombustible threads as part of the media.  So separators for these filter packs are not called out.

        - ******************************************************************************

Separators (for Type A Filter Packs only): ​​​<< Coated; or  Uncoated>>​​​ Aluminum.

Materials of construction

General

The following are unacceptable materials of construction:  particle board, asbestos, cadmium-coated metals, and any material that generates EPA regulated wastes as specified in <<40 CFR 261>>.

Filter Media

Manufacture silicate media in accordance with <<ASME AG-1>>, Article FK-3130.

        - ******************************************************************************

        - The following is a designer choice.

        - ******************************************************************************

Separatorless filter packs shall use formed media to fulfill the function of the separator.

      - ***************************************************************************************

      - The following 4 paragraphs are designer choices.

      - ***************************************************************************************

End Caps, Grilles, and Flanges for Type 1 Filters

Stainless Steel, Type ​<< 304; or  316>>​, minimum 18 gauge in accordance with <<ASME AG-1>>, Article FK-3110 and Article FK-4121.

Case for Type 2 Filters

Stainless Steel, Type << 304; or  316>>, minimum 14 gauge in accordance with <<ASME AG-1>>​​, Article FK-3110 and Article FK-4122.

Case for Type 4 Filters

Stainless Steel, Type << 304; or  316>>, minimum 14 gauge in accordance with <<ASME AG-1>> ASM, Article FK-3110 and Article FK-4123.

        - ******************************************************************************

        - Before specifying wood-case filters, verify that they are still allowed under the current combustible load analysis for the facility.  Facilities with large filter plenums may now be restricting the use of wood-case HEPA filters.   Note:  Wood-case filters generally cost less than metal-case filters but are more likely to be rejected during receipt inspection due to being out of square. Also, metal-case filters weigh approximately 50% more than wood-case filters, so ensure mounting frames can support the additional weight.

        - ******************************************************************************

Plywood in accordance with <<ASME AG-1>>, Article FK-3110 (a) (marine plywood), or Article FK-3110 (b) (exterior plywood).

Fasteners (when used)

Use fasteners that are in accordance with <<DOE-STD-3020>> (Section 5.3.7).

      - ***************************************************************************************

      - Select only one type of separator per filter Type.

      - ***************************************************************************************

Separators (when used)

Aluminum, conforming to <<ASME AG-1>>, Article FK-3160, (a).

Acid Resistant Aluminum, conforming to <<ASME AG-1>>, Article FK-3160, (b).

Glass Ribbon, conforming to <<ASME AG-1>>, Article FK-3160, (c).

String, conforming to <<ASME AG-1>>, Article FK-3160, (d).

Hot Melt, conforming to <<ASME AG-1>>, Article FK-3160, (e).

      - ***************************************************************************************

      - A single splice is allowed only for Type 1 HEPA filters.  No other filters are allowed to have splices.

      - ***************************************************************************************

Adhesives used to​<< splice the media,; or  None - N/A>>​ fasten gaskets to filter case, and seal the filter pack or faceguards to the case.

Self-extinguishing in accordance with <<ASME AG-1>>, Article FK-3150.

Gaskets and Seals

        - ******************************************************************************

        - Select only one type of gasket.

        - ******************************************************************************

Elastomer Gasket – in accordance with <<ASME AG-1>>, Article FK-3121.

        - *** OR ***

Gelatinous Seal – in accordance with <<ASME AG-1>>, Article FK-3122.

      - ***************************************************************************************

      - Faceguards only apply to Type 2 and Type 4 filters.

      - ***************************************************************************************

Faceguards

        - ******************************************************************************

        - Specify Type 304 stainless steel for highly-corrosive atmospheres.

        - ******************************************************************************

Faceguards – galvanized steel in accordance with <<ASME AG-1>>, Article FK-3140.

Faceguards -Type 304 stainless steel in accordance with <<ASME AG-1>>, Article FK-3140.

      - ***************************************************************************************

      - Grilles only apply to Type 1 filters.

      - ***************************************************************************************

Grilles

Grilles - in accordance with <<ASME AG-1>>, Article FK-3170.

Fabrication

General

Fabricate in accordance with <<ASME AG-1>>, Articles FK-6000, <<DOE-STD-3020>> (Section 5.4), and <<ASME NQA-1>>-2008 with 2009 addenda.

        - ******************************************************************************

        - The following 5 subparagraphs are designer choices.

        - ******************************************************************************

Install faceguards on each face of all Type 2 and Type 4 filters.  Install faceguards such that they are held firmly in-place, do not interfere with the sealing of the gasket, and do not pose a puncture hazard to personnel handling the filter.

Install ​​​<< internal; or  external>>​​​ elastomer gasket on Type 1 HEPA filters in accordance with <<ASME AG-1>>, Article FK-4141.

Install ​<< internal; or  external>>​ gelatinous seal gasket on Type 1 HEPA filters in accordance with <<ASME AG-1>>, Article FK-4142.

Install elastomer gasket on ​<< upstream;  downstream;  both ; and  faces>>​ of Type 2 and Type 4 HEPA filters in accordance with <<ASME AG-1>>, Article FK-4141.

Install gelatinous seal gasket on ​<< upstream; and  downstream>>​ face of Type 2 and Type 4 HEPA filters in accordance with <<ASME AG-1>>, Article FK-4142.

        - ******************************************************************************

        - The labeling includes a UL label indicating successful testing per UL-586. The UL label is required for all qualified HEPA filters.

        - ******************************************************************************

Label each filter and shipping container (carton containing one filter) in accordance with <<DOE-STD-3020>>​ (Section 6.1.6). Labels must be permanently affixed to the filter.

QUALIFICATION AND Acceptance testing

      - ***************************************************************************************

      - As of the date of this Master Specification Section, no Section FK Type 1 HEPA filters have been qualified by any of the three manufacturers from which LANL usually buys filters. However, both Type 2 and Type 4 filters may be deemed qualified based on the qualification of a filter size listed in ASME AG-1, Section FC, Table FC-4110-1. The filters listed in the Specifier’s Reference webposted under Section << 23 4133.13 - HEPA Filters – ASME AG-1, Section FC>> in LANL Engineering Standards Specifications Website are all HEPA filters that have been qualified to Article 5000 of ASME AG-1, Section FC.

      - These filters can be used as the basis for determining if a Type 2 or Type 4 Section FK filter is eligible to be considered qualified. See Section FK, Article FK-5200 and Article FK-5400, and DOE-STD-3020-2015 (Section 6.1.2) for guidance on determining how to use the information contained in the Specifier’s Reference for Safety Class (ML-1) and Safety Significant (ML-2) applications require that a qualified filter be specified.

      - ***************************************************************************************

Have qualification testing of filters and filter media performed by an independent test facility in accordance with <<ASME AG-1>>, Article FK-5000 (with <<DOE-STD-3020>>, Section 6.1.2 allowances) prior to start of manufacturing of filters for this purchase.

Perform factory inspection of filters in accordance with <<ASME AG-1>>, Article FK-5500.  Additionally, LANL will be inspecting Type 4 filters to LANL QPA-RIT-WI-002.007 (see Appendix A of this Section, specifically Attachment 1, Table 2 for inspection criteria). Filters that do not meet these inspection criteria will be rejected.

Perform factory production testing of aerosol penetration and resistance to air flow for each filter in accordance with <<ASME AG-1>>, Article FK-5600.

Ship filters to the FTF (Air Techniques International Testing Laboratories, Suite 104, 1708 Whitehead Rd., Baltimore, MD 21207, phone 410-277-8981, fax 410-277-3448, email ATITL@atitest.com) to have inspection and performance acceptance testing performed in accordance with <<ASME AG-1>>, Article FK-5600, ​​<< and; or  None - N/A>>​​ <<DOE-STD-3020>>​, and LANL QPA-RIT-WI-002.007, Table 2 (see Appendix A of this Section) for Type 4 filters. Filters that do not meet these inspection criteria are not acceptable.

PART 3 - execution (performed by AND AT lanl)

Examination

      - ***************************************************************************************

      - The following two paragraphs are designer choices.

      - ***************************************************************************************

Inspect all <<ASME AG-1>> Section FK, Type 4 filters upon shipment receipt to LANL QA-RIT-WI-002.007. Verify documentation from Article ​​​<< 1.7; or  ___>>​​​, Action Submittals, is included and is complete.

Inspect all <<ASME AG-1>> Section FK, Type 1 and 2 filters upon shipment receipt to the requirements contained on LANL Form 1952.  Verify documentation from Article ​​<< 1.7; or  ___>>​​, Action Submittals, is included and is complete.

Storage

Store filters in accordance with <<ASME AG-1>> Article FK-7000, <<DOE-HDBK-1169>>, Appendix A or in accordance with the manufacturer’s requirements, whichever is more restrictive, and

Store filters properly oriented, as indicated on shipping container.

When stored out of the shipping container, stagger the box pattern on each level so as to not have columns of boxes that can easily topple.

Shelf life: Do not store filters for more than 10 years after manufacture date.

Handling and installation

Handle and install HEPA filters in accordance with <<DOE-HDBK-1169>>, Appendix A, Parts A.5 and A.6.

Field Quality control

Test filters after installation for leakage in accordance with LANL requirements.

Replace all filters that fail LANL in-place leakage test.

Notify Seller, Purchasing Group, and Quality Assurance Group of filter rejections and re-evaluate the future procurement status of that manufacturer and/or model.

    - **********************************************************************************************

      - Appendix A is to be included with all ML-1, ML-2, and ML-3 filter procurements; verify that it is latest at https://int.lanl.gov/org/ddops/aldbus/si/dcrm/dcrm-docs/IQPA/QPA-RIT-WI-002.pdf (LANL only). Update as required.

    - **********************************************************************************************

end of main section; appendiX followS

end of section

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 23 4133.16, REV. 1, DATED APRIL 15, 2026.

END OF SECTION