Section 25 0519 
Low Voltage Electrical Conductors and Cables for BAS Electrical Systems

  - ************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 3 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) I&C POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable Sections from all Divisions, especially Division 1, General requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality sections.

      - NOTE: This Section overrides Division 26 electrical installation requirements for BAS systems only. If the designer wishes to use Division 26 installation requirements for specific portions of the BAS design, then these must be clearly noted on the drawings as a deviation from this Section.

  - ************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

Conductors and cable used for low voltage (<100 VDC and < 50 VAC) building automation systems (BAS)

BAS wire (600 V/300 V)

BAS cable (300 V)

Wire and cable connectors

Wire pulling lubricant

RELATED REQUIREMENTS

Section << 01 2500 - Substitution Procedures>>

Section << 01 3300 - Submittal Procedures>>

Section << 25 0553 - Identification for BAS Electrical Systems>>

REFERENCE STANDARDS

NECA 1 - Standard for Good Workmanship in Electrical Construction.

NFPA 70 - National Electrical Code.

UL 486A-486B - Wire Connectors.

ACTION SUBMITTALS

Submit the following per Section << 01 3300 - Submittal Procedures>>​

Catalog Data: BAS wire

Catalog Data: BAS cable

Catalog Data: Compression connectors.

        - NOTE: Submittals not required when supplying parts specifically called out on design drawings or listed by manufacturer and model number in LANL’s standard BAS product list.

QUALITY ASSURANCE

Comply with the <<NFPA 70>> (NEC) for installation requirements.

Provide products that are listed and labeled by a Nationally Recognized Testing Laboratory (NRTL).

DELIVERY, STORAGE AND HANDLING

Receive, store, protect, and handle products per <<NECA 1>>.

PART 2 - PRODUCTS

    - **********************************************************************************************

      - The following Article in PART 2 is a designer-choice to allow for product substitutions.

    - **********************************************************************************************

PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section << 01 2500 - Substitution Procedures>>.

WIRE FOR BAS APPLICATIONS

Provide NRTL-Listed wire with the following characteristics:

Description:

Single-conductor, 600 V insulated wire.

Conductor:

18 to 14 AWG Copper

Stranded

Insulation Type:

Type THHN/THWN-2 Per UL Standard 83

Type MTW per UL Standard 1063

Type TFFN per UL Standard 1408

Type MTW per UL Standard 1015. Used in BAS control panel fabrication only

Exceptions:

If alternate types or sizes are specified on the Drawings they shall be used in place of the above.

If the BAS manufacturer installation instructions indicate alternate type or sizes are required for installation, they shall be used in place of the above.

Color-code conductors as follows:

Use the following color codes for low-voltage Class 2 power system conductors:

          - Positive DC: Red

          - Ungrounded AC: Yellow

          - Negative DC: Black

          - Grounded AC: Blue

Exception: If colors are specified on the Drawings, they shall override the colors above.

CABLE FOR BAS APPLICATIONS

Provide NRTL-listed cable with the following characteristics:

Description:

Multi-conductor 300 V insulated cables.

Multi-conductor 600 V insulated cables where the separation distances and requirements of <<NFPA 70>>, Article 725.136 cannot be met, or, when the cable required for the application is only available with 600 V insulation.

Conductor:

22 to 18 AWG Copper

Stranded

Shield with drain wire when specified in drawings

Maximum 12 conductors plus a shield conductor per cable

Cables used for BACnet MSTP, Arcnet, MODBUS RTU, and similar RS-485 type communications shall be 2 conductors, shielded, twisted pair, low capacitance (~22pF/ft) cable unless specified otherwise in Drawings. Cables used for this type of application shall have an orange outer jacket.

Cable Type:

All cable types approved under <<NFPA 70>> when installed per <<NFPA 70>> requirements.

        - ******************************************************************************

        - The following Exceptions subparagraph is a designer-choice and refers to Types and Sizes other than those specified on the drawings or called out by the BAS Manufacturer.

        - ******************************************************************************

Exceptions:

If alternate types or sizes are specified on the Drawings, they shall be used in place of the above specifications in paragraph << 2.3.A; or  _______>>.

If the BAS manufacturer installation instructions indicate alternate type or sizes are required for installation, they shall be used in place of the above specifications in paragraph. << 2.3.A; or  _______>>.

Color-code conductors as follows:

Use the following color codes for low-voltage Class 2 power system conductors found in cables:

          - Positive DC or Ungrounded AC: Red

          - Negative DC or Grounded AC: Black or Green

          - Signal Wire: White

          - Network Wire + Signal: White or Red

          - Network Wire – Signal: Black

Use the following color codes for standard thermostat connections as follows:

          - 24 VAC: Red

          - Fan: Green

          - Heat:  White

          - Cool: Yellow

          - Compressor: Yellow

          - Rev Valve: Orange

          - Common: Blue or Black

        - ******************************************************************************

        - The following Exceptions subparagraph is a designer-choice to allow for alternate Colors Coded Conductors than those specified on the drawings.

        - ******************************************************************************

Exceptions

If the alternate colors codes are specified on the drawings or dictated by the BAS manufacturer’s standard installation recommendations, they shall be used in place of color codes specified in paragraph << 2.3.B; or  _______>>

WIRING CONNECTORS

For control wiring, use nylon-insulated, crimp-on terminals with insulation grip that meet the requirements of <<UL 486A-486B>>.

Manufacturer:

3M “Scotchlok MNG”

Thomas & Betts “Sta-Kon”

Terminals:

Use ring tongue terminals for nutted studs.

Use flanged fork terminals for barrier terminal blocks.

Insulation-piercing-type connectors are not acceptable for power or control wiring.

      - ***************************************************************************************

      - The following paragraphs and subparagraphs are designer-choice to allow for exceptions for alternate Wiring Connectors.

      - ***************************************************************************************

Exceptions:

Wiring connectors are not required where wires terminate in cage clamp, pressure plate or equivalent terminals.

Insulation-piercing type connectors may be used to connect Ethernet/RJ type connectors when installed using the correct installation tools for the connector type.

Devices with pigtails may be terminated using wire nuts.

WIRE-PULLING LUBRICANT

Provide NRTL-listed wire pulling lubricant that is compatible with the conductor insulation or jacket, has a maximum coefficient of dynamic friction of 0.25, and leaves no flammable residue. For cold weather installations, provide wire pulling lubricant suitable for conduit temperature.

PART 3 - EXECUTION

    - **********************************************************************************************

      - The following Articles Examination, Preparation, Existing Work are designer-choice. Designer should select only those which apply to the project.

    - **********************************************************************************************

EXAMINATION

      - ***************************************************************************************

      - The following paragraphs and subparagraphs are designer-choice.

      - ***************************************************************************************

Verify that work of other trades likely to damage wire and cable is completed.

Verify raceway installation is complete and supported.

Wire and cable routing shown on Drawings is approximate unless dimensioned.

Route wire and cable as required to meet project conditions.

Where cable routing is not shown, and destination only is indicated, determine exact routing and lengths required to meet Project conditions.

PREPARATION

Examine raceways and building finishes that are to receive wires and cables for compliance with installation tolerances and other conditions. Do not proceed with installation until unsatisfactory conditions have been corrected.

Do not handle or pull cables that are colder than +14 degrees F. Store cold cables for at least 24 hours in a heated building prior to installation.

EXISTING WORK

      - ***************************************************************************************

      - The following paragraphs and subparagraphs are designer-choice and apply to Existing Wire and Cable to be removed or abandoned.

      - ***************************************************************************************

Remove abandoned wire and cable associated with the BAS control system or its previous electric control system, including abandoned wire and cable above accessible ceiling finishes. Patch surfaces where removed cables pass through building finishes when specified on Drawings.

Exception: If Drawings specify that existing wire is to remain.

Disconnect abandoned circuits feeding controls and remove circuit wire and cable. Remove abandoned boxes when wire and cable servicing boxes are abandoned and removed. Install blank cover for abandoned boxes not removed.

Exception: If Drawings specify that existing conduit and boxes are to remain.

Provide access to existing wiring connections remaining active and requiring access. Modify installation or install access panel.

Extend existing circuits using materials and methods as specified.

BAS WIRE AND CABLE INSTALLATION

Install building wire according to the <<NFPA 70>> , the requirements in this Section, and, as applicable, <<NECA 1>>.

Do not damage conductor, insulation, or jacket by excessive installation pulling tension or sidewall bearing pressure.

Do not “through-pull” conductors at boxes, fittings, or cabinets where a change of raceway alignment occurs.

Terminate cable ends neatly by removing exposed parts of shielding (not drain wire) and splitting strings or reinforcing strings.

Terminate cable shielding drain conductor at one end only. Unless specified otherwise on drawings the controller end of the shield shall be the grounded end.

At un-terminated end of cable shielding drain conductor, ensure the drain conductor is insulated from possible contact with grounded surfaces with insulating tape or heat shrink tubing. Leave at least 1/2-inch length of drain conductor under the insulation for future testing needs.

      - ***************************************************************************************

      - The following paragraphs are designer-choice and apply to Cable Assemblies and Splicing.

      - ***************************************************************************************

Do not cut off unused conductors in cable assemblies. Either bundle the spare conductors neatly or twist them back around the cable for future use.

Cables shall not be spliced without special permission from LANL ES I&C responsible engineer. Splicing is allowed if specifically called out on the Drawings.

CONNECTOR INSTALLATION

Install conductors in terminals, splices, adapters, and connectors in accordance with the manufacturer’s instructions. Have the manufacturer’s installation instructions available at the construction site.

Do not nick inner wire insulation when removing cable outer covering or shielding.

Do not nick conductors when removing insulation.

Do not cut conductor strands to fit into connectors, splices, adapters, or terminals.

IDENTIFICATION

Identify wire and cable under provisions of Section << 25 0553 - Identification for BAS Electrical Systems>>.

FIELD QUALITY CONTROL

      - ***************************************************************************************

      - The following paragraphs and subparagraphs are designer-choice and apply to observing conductor and cable installations.

      - ***************************************************************************************

Observe conductors and cables during the installation process.

Reject and replace entire reels, rolls, or boxes containing conductors or cables with material or manufacturing defects.

Reject and replace cable or conductor segments that have been kinked, dented, or otherwise damaged during handling or installation.

Perform the following inspections

Inspect conductors and cables for:

          - **********************************************************************

          - The following subparagraph is a designer-choice for the inspection of all cable and conductors used.

          - **********************************************************************

Freedom from material defect or physical damage,

Correct conductor size, material, and insulation type,

Correct color coding and identification.

Inspect connections for:

Correct connector size and type, according to the Specifications.

      - ***************************************************************************************

      - The following paragraphs and subparagraphs are designer-choice to included the testing of cables and conductors.

      - ***************************************************************************************

Perform the following tests:

After connecting conductors to equipment, verify correct connection of each control circuit conductor through point-to-point testing.

Perform a tug-test on all terminal block connections by lighting pulling on each individual wire. Any wire found to be loose shall be re-terminated and re-tested.

Remove and replace defective, incorrect, or improperly installed conductors and connectors. Re-inspect and re-test replacement conductors and connectors.

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 25 0519, REV. 3, DATED APRIL 15, 2026.