Section 25 0533 
Raceways and Boxes for BAS Electrical Systems

  - ************************************************************************************************************

    - LANL MASTER SPECIFICATION section

Rev. 2 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., SECTION INCLUDES in PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) I&C POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality sections.

      - NOTE: This section overrides Division 26 electrical installation requirements for BAS systems only. If the designer wishes to use Division 26 installation requirements for specific portions of the BAS design, then these must be clearly noted on the drawings as a deviation from this section requirement.

  - ************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

Intermediate metal conduit and fittings.

Rigid metal conduit and fittings.

Electrical metallic tubing and fittings.

Flexible metal conduit and fittings.

Liquid-tight flexible metal conduit and fittings

Insulating bushings.

Grounding bushings.

Surface metal raceway.

Wireway.

Outlet boxes.

Pull and junction boxes.

Expansion fittings.

      - ***************************************************************************************

      - The following paragraph is a designer-choice. Retain when raceway seals are required for project.

      - ***************************************************************************************

Raceway seals.

Corrosion protection tape.

RELATED REQUIREMENTS

Section << 01 2500 - Substitution Procedures>>.

Section << 01 3300 - Submittal Procedures>>​.

Section ​<< 07 8400 - Firestopping>>​

Section << 25 0553 - Identification for BAS Electrical Systems>>

Section << 26 0529 - Hangers and Supports for Electrical Systems>>

Section << 26 0548.16 - Seismic Controls for Electrical Systems>>.

REFERENCE STANDARDS

ANSI C80.1 - American National Standard for Electrical Rigid Steel Conduit (ERSC).

ANSI C80.3 - American National Standard for Electrical Metallic Tubing -- Steel (EMT-S).

ANSI C80.6 - American National Standard for Electrical Intermediate Metal Conduit.

ASCE 7 - Minimum Design Loads and Associated Criteria for Buildings and Other Structures.

ASHRAE 90.1 - Energy Standards for Buildings Except Low-Rise Residential Buildings.

NECA 1 - Standard for Good Workmanship in Electrical Construction.

NEMA FB 1 - Fittings, Cast Metal Boxes, and Conduit Bodies for Conduit, Electrical Metallic Tubing, and Cable.

NEMA OS 1 - Sheet-Steel Outlet Boxes, Device Boxes, Covers, and Box Supports.

NEMA OS 3 - Selection and Installation Guidelines for Electrical Outlet Boxes.

NFPA 70 - National Electrical Code.

SMACNA (DCS) - HVAC Duct Construction Standards Metal and Flexible.

UL 1 - Flexible Metal Conduit.

UL 5 - Surface Metal Raceways and Fittings.

UL 6 - Electrical Rigid Metal Conduit-Steel.

UL 50 - Enclosures for Electrical Equipment, Non-Environmental Considerations.

UL 360 - Liquid-Tight Flexible Metal Conduit.

UL 498 - Attachment Plugs and Receptacles.

UL 514A - Metallic Outlet Boxes.

UL 514B - Conduit, Tubing, and Cable Fittings.

UL 797 - Electrical Metallic Tubing-Steel.

UL 1203 - Explosion-Proof and Dust-Ignition-Proof Electrical Equipment for Use in Hazardous (Classified) Locations.

UL 1242 - Electrical Intermediate Metal Conduit-Steel.

APPLICABILITY

Raceways and boxes used for low voltage (< 100VDC and < 50VAC) building automation systems (BAS).

      - ***************************************************************************************

      - The following Article Action Submittals is a designer-choice.

      - ***************************************************************************************

ACTION SUBMITTALS

Submit the following per Section ​<< 01 3300 - Submittal Procedures>>​​:

Catalog Data: Submit catalog data describing surface metal raceway. Include data substantiating that materials comply with specified requirements.

Catalog Data: Submit catalog data describing wireway. Include data substantiating that materials comply with specified requirements.

QUALITY ASSURANCE

Comply with the <<NFPA 70>> for installation requirements.

Provide products that are listed and labeled by a Nationally Recognized Testing Laboratory (NRTL).

DELIVERY, STORAGE AND HANDLING

Receive, store, and protect, and handle products according to <<NECA 1>>.

PART 2 - PRODUCTS

    - **********************************************************************************************

      - The following Article in PART 2 is a designer-choice to allow for product substitutions.

    - **********************************************************************************************

PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section << 01 2500 - Substitution Procedures>>.

SEISMIC PERFORMANCE REQUIREMENTS

      - ***************************************************************************************

      - The seismic exemptions noted below are based on ASCE 7-16. If the Code of Record for the project refers to a different version of ASCE 7, the designer is responsible to check the seismic design requirements per that applicable edition.

      - ***************************************************************************************

Note to Constructor: Component importance factor of 1.0 is default unless noted otherwise on engineering drawings.

The following nonstructural components (raceways and/or boxes) are seismically exempt per <<ASCE 7>>, Section 13.1.4, but shall be positively attached to the structure provided that:

Component weighs 400 lbs or less with center of mass located 4 ft or less above the adjacent floor level, flexible connections are provided between the component and associated ductwork, piping and conduit, and component importance factor is equal to 1.0 or

Component weights 20 lbs or less, and in the case of a distributed system 5 lbs/ft or less.

For components outside the above exemptions, constructor to consult design engineer for seismic support design requirements, if supports not designed during detailed design phase of project.

For conduits less than 2.5 inch trade size, supports are seismically-exempt per <<ASCE 7>>, Section 13.6.5. For conduits 2.5 inch trade size or greater, constructor to consult design engineer for seismic support design requirements, if supports not designed during detailed design phase of project.

Trapeze assemblies or individual rod hangers supporting raceways with component importance factor of 1.0 that comply with <<ASCE 7>>, Section 13.6.5 Exceptions are seismically-exempt. For all other trapeze assemblies or individual rod hangers supporting raceways, constructor to consult design engineer for seismic support design requirements, if supports not designed during detailed design phase of project.

SIZING

When specific sizes for raceways, electrical j-boxes and enclosures are not specified in the design drawings, it is the installer’s responsibility to size such items to accommodate the required number of cables and wires to not exceed <<NFPA 70>> maximum fill requirements.

When placing cables in raceways, the outside dimension of the cable shall be used to determine fill cross sections.

BAS control cables and wires are not considered current carrying conductors and thus are not subject to <<NFPA 70>> Table 310.15(C)(1) (2020) adjustment factors.

INTERMEDIATE METAL CONDUIT AND FITTINGS (IMC)

Furnish intermediate metal conduit (IMC), nipples, elbows and couplings that conform to <<UL 1242>> and <<ANSI C80.6>>.

Furnish zinc-plated, threaded, malleable iron fittings and conduit bodies that meet the requirements of <<UL 514B>>, and <<NEMA FB 1>>.

RIGID METAL CONDUIT AND FITTINGS (RMC)

Furnish rigid metal conduit (RMC) that meets the requirements of <<UL 6>> and <<ANSI C80.1>>.

Furnish zinc-plated, threaded, malleable iron fittings and conduit bodies that meet the requirements of <<UL 514B>> and <<NEMA FB 1>>.

ELECTRICAL METALLIC TUBING AND FITTINGS (EMT)

Furnish galvanized electrical metallic tubing (EMT) that conforms to <<UL 797>>​ and <<ANSI C80.3>>.

EMT raceway trade size 1 and smaller shall be blue in color to distinguish the raceway as BAS controls. Reused existing IMC does not need to be replaced to meet this requirement.

Furnish compression or set-screw type fittings that meet the requirements of <<UL 514B>>, and <<NEMA FB 1>>. Furnish insulated throat connectors.

FLEXIBLE METAL CONDUIT AND FITTINGS

Furnish galvanized steel flexible metal conduit that meets the requirements of <<UL 1>>.

Furnish zinc-plated malleable iron fittings that meet the requirements of <<UL 514B>>, and ANSI/<<NEMA FB 1>>. Furnish insulated throat connectors.

LIQUID-TIGHT FLEXIBLE METAL CONDUIT AND FITTINGS

Furnish liquid-tight flexible metal conduit that meets the requirements of <<UL 360>>.

Furnish zinc-plated malleable iron or zinc-plated steel liquid-tight fittings that meet the requirements of <<UL 514B>>, and <<NEMA FB 1>>. Furnish insulated throat connectors.

INSULATING BUSHINGS

Provide NRTL listed insulating bushings with 105 degrees C rated insulation.

Manufacturer: O-Z/Gedney, Type IB.

GROUNDING BUSHINGS

Provide 150 degrees C rated insulated throat grounding bushings with lay-in type ground cable lugs.

SURFACE METAL RACEWAY

Furnish surface metal raceway that meets the requirements of <<UL 5>>.

Furnish surface metal raceway fabricated from cold rolled galvanized steel with a thickness of not less than 0.040 inches and coated with a baked-enamel finish.

Furnish fittings required for a complete installation.

Manufacturer: Wiremold “500” or “700” series.

WIREWAY

Provide ​​<< general purpose;  oil-tight and dust-tight; or  rain-tight>>​​ type wireway with covers, elbows, tees, and fittings required for a complete system.

OUTLET BOXES

Provide outlet boxes selected for specific installations using the guidance in <<NEMA OS 3>>, and the requirements of this Section.

      - ***************************************************************************************

      - The following paragraphs are a designer-choice for DRY and DAMP/WET locations. Designer should select based on project applications.

      - ***************************************************************************************

For dry locations provide galvanized steel outlet boxes that comply with <<UL 514A>> and <<NEMA OS 1>>.

        - ******************************************************************************

        - The following subparagraphs are designer-choice.

        - ******************************************************************************

For flush outlets in stud walls or above-grade cast-in-place concrete walls, use 4-inch square boxes. Provide raised device covers that match the thickness of the wallboard and the number of devices. Provide supplemental box supports to prevent movement of the box.

For flush outlets in above-grade masonry walls use masonry boxes with knockouts. Provide boxes with depth suitable for the masonry unit size. Provide multiple gang boxes as required by the number of devices.

For surface outlet boxes in EMT raceway systems, use 4-inch square boxes. Provide square surface covers that match the installed device and have not less than two holes for securing the device to the cover.

For damp or wet locations and for surface-mounted RMC or IMC raceway systems, provide outlet boxes that comply with <<UL 498>> and <<UL 514A>>, <<NEMA FB 1>>.

For flush or surface wall-mounted outlets, use cast gray or malleable iron boxes with threaded hubs. Provide multiple gang boxes as required to fit devices. Provide gasketed cast gray or malleable iron or cast copper-free aluminum covers that match the installed device and have not less than two holes for securing the device to the cover.

PULL AND JUNCTION BOXES

      - ***************************************************************************************

      - The following paragraphs are designer-choice. Designer should select the environmental requirements based on the installation location that apply.

      - ***************************************************************************************

For dry locations in clean, non-contamination environments use galvanized sheet steel pull and junction boxes that comply with<<UL 50>>​​​​ Type 1 and the <<NFPA 70>> as to size and construction. Use boxes not less than 4 inches square x 1-1/2 inches deep with screw-secured covers. Provide larger boxes as required by the number and size of raceways and conductors.

For dry locations in dusty or possible contamination (e.g. beryllium, explosives, or uranium) environments use galvanized steel that comply with <<UL 50>>  Type 12 and the <<NFPA 70>> (NEC) as to size and construction. Use boxes not less than 6 inches square x 4 inches deep with gasketed covers. Provide larger boxes as required by the number and size of raceways and conductors.

For damp or wet, non-corrosive locations, in raceway runs up to 3/4 inch trade size, provide cast gray or malleable iron pull and junction boxes with threaded hubs and gasketed cast gray or malleable iron or cast copper-free aluminum covers.

For damp or wet, non-corrosive locations, in raceway runs 1 inch trade size and larger, provide galvanized sheet-steel pull and junction boxes and covers that comply with<<UL 50>> Type 3R.

Provide boxes that have connection points for equipment grounding conductors.

EXPANSION FITTINGS

Furnish expansion fittings with hot dipped galvanized malleable iron body, factory installed packing and a bonding jumper.

Manufacturer: O-Z/Gedney, Type AX, TX or EXE with Type BJ bonding jumper.

      - ***************************************************************************************

      - The following Article is a designer-choice. Retain when raceway seals are required for project.

      - ***************************************************************************************

RACEWAY SEALS

      - ***************************************************************************************

      - The following paragraphs are designer-choice. Designer should select if raceway seals are applicable to the project and their resulting environmental requirements.

      - ***************************************************************************************

Raceway Sealant for use in temperature differences, radiological, or moisture control

Furnish a two-part, foam-based, raceway sealing system.

Provide sealing compound specifically listed for use with the foam damming materials.

Provide sealing compound that is identified for use with the conductor or cable insulation.

Manufacturer: Polywater FST-MINI for raceways up to 2 inches.

Manufacturer: Polywater FST-250 for raceways 2 inches to 8 inches.

Sealing Fittings for Use in Hazardous-Classified Locations

Furnish zinc-plated, malleable iron sealing fittings that meet the requirements of <<UL 1203>> for use in Hazardous (Classified) Locations.

Select each sealing fitting so the cross-sectional area of conductors passing through the seal is not more than 25 percent of the cross-sectional area of a rigid metal conduit of the same trade size unless the fitting is specifically identified for a higher percentage of fill.

Provide sealing compound specifically listed for use with the sealing fitting.

Manufacturer: Crouse-Hinds Type EYS, EYSX, EYD.

CORROSION PROTECTION TAPE

Furnish pressure-sensitive, 10 mil thick. PVC based tape for corrosion protection of metal raceway and fittings.

Manufacturer: 3M, Type 50.

FINISHES

Provide products with zinc coating or with treatment of equivalent corrosion resistance using approved alternative treatment, finish, or inherent material characteristic that is suitable for the environment in which the product will be installed and used.

PART 3 - EXECUTION

    - **********************************************************************************************

      - The following Articles Existing Work and Examination are designer-choice

    - **********************************************************************************************

EXISTING WORK

      - ***************************************************************************************

      - The following paragraphs are designer-choice based on project-specific requirements.

      - ***************************************************************************************

Cap, plug, or seal remaining raceway openings to restore the original fire rating of floors, walls, and ceilings after electrical demolition.

Maintain access to existing boxes and other installations remaining active and requiring access. Modify installation or provide access panel.

Extend existing raceway and box installations using materials and methods compatible with existing electrical installations, or as specified.

Clean and repair existing raceway and boxes to remain or to be reinstalled.

EXAMINATION

Examine surfaces to receive raceways and boxes for compliance with installation tolerances and other conditions affecting performance of the raceway system. Do not proceed with installation until unsatisfactory conditions have been corrected.

GENERAL

Install complete systems of raceways and boxes for wiring systems.

Install raceways and boxes according to <<NECA 1>>, <<NECA 101>>, <<NECA 111>>, the <<NFPA 70>>, the manufacturer’s instructions, and requirements in this Section.

Raceway termination points and box locations shown on the Drawings are in approximate locations unless dimensioned. Verify locations before rough-in.

Raceway routing is shown on the Drawings in approximate locations unless dimensioned.  Coordinate routing with structure and with work of other trades. Route as required for a complete wiring system.

Support raceways and boxes in accordance with the requirements of the <<NFPA 70>>, Section << 26 0529 - Hangers and Supports for Electrical Systems>>, and Section << 26 0548.16 - Seismic Controls for Electrical Systems>>.

Identify boxes as required in Section << 25 0553 - Identification for BAS Electrical Systems>>.

Raceways used for BAS shall be marked with blue tape of at least 1/2 inch width or approved equivalent as follows:

At each termination end of a raceway run within 12 inch of the termination.

Every 20 feet for all conduit runs longer than 30 feet in length.

When used on exterior raceways use tape approved for outdoor use or use blue colored paint.

Raceways provided with a blue color do not need additional tape markings.

Flexible raceways do not need blue markers.

Raceways in concealed wall cavities, under ground or in other inaccessible locations do not require blue markings

Wireways shall be marked per Section << 25 0553 - Identification for BAS Electrical Systems>> with Enclosure Nameplates and Voltage Markers only. No blue markers are required.

Arrange raceway and boxes to maintain headroom and present neat appearance.

Install knockout closures in unused openings in boxes or raceways.

      - ***************************************************************************************​

      - The following Articles Raceway Installation, Firestopping, Outlet Box Installation, Pull and Junction Box Installation, Wireway Installation, Surface Metal Raceway Installation are designer-choice based on project-specific requirements.

      - ***************************************************************************************

RACEWAY INSTALLATION

For BAS low voltage wiring systems (less than 100 volts) use raceway materials according to the <<NFPA 70>> and the following:

        - ******************************************************************************

        - The following subparagraphs are designer-choice based on raceway environmental requirements.

        - ******************************************************************************

Outdoors - Underground:

Direct buried: Use PVC, tape-wrapped RMC, or tape-wrapped IMC. Do not use PVC where subject to physical damage. Install with 24 inches minimum cover from top of raceway to finished grade or top of paving.

Under 2 inches of concrete: Use PVC, RMC, or IMC for concrete encased underground work. Install with 12 inches minimum cover from top of raceway to finished grade or paving.

Outdoors - Exposed: Use RMC or IMC.

Outdoor corrosive locations (including cooling towers): Use Reinforced Thermosetting Resin Conduit (RTRC) and fittings.

Outdoors - Concealed: Use RMC or IMC for concealed outdoor work. Do not use bare RMC or IMC in direct contact with earth. EMT may be used for concealed outdoor work where not in contact with earth, not encased in concrete, and where not exposed to deteriorating agents.

Indoors – Exposed outside of designated electrical rooms or telecommunications rooms:

Exposed to severe physical damage during or after installation: Use RMC or IMC.

Exposed to moisture: Use RMC or IMC.

Exposed to corrosives: Use Reinforced Thermosetting Resin Conduit (RTRC) and fittings.

Not exposed to deteriorating agents and not subject to severe physical damage during or after installation: Use RMC, IMC, or EMT.

Indoors – Concealed:

Within drywall partitions and above false ceilings: Use RMC, IMC, or EMT.

Within masonry or cast-in-place concrete walls or floors: Use RMC or IMC.

Direct-buried under building floor slabs on grade: Use PVC, tape-wrapped RMC, or tape-wrapped IMC. Locate top of raceways not less than 12 inches below the bottom of the concrete slab. Install warning tape approximately 6 inches above the raceways; install multiple warning tapes above parallel raceway runs wider than 18 inches.

Under building floor slabs on grade: Use PVC, RMC, or IMC.

On Ductwork

          - **********************************************************************

          - The following subparagraphs are designer-choice and apply to Ductwork Installations.

          - **********************************************************************

Short lengths of raceway, up to Trade Size 1, may be supported by ductwork provided the following are met:

The raceway run supported on the ductwork is no longer than 10 feet in length.

The raceway dead-ends at a device(s) associated with the supporting ductwork, e.g., sensor, damper actuator, valve actuator, etc.

Any flex connector in the ductwork is bridged by a flex connection in the raceway.

The raceway contains only Class 2 circuits.

Existing Ductwork: Seal penetrations into the duct work per  <<SMACNA (DCS)>> based on existing seal class installed.

New Ductwork: Seal penetrations into the ductwork per <<ASHRAE 90.1>> requirements.

Do not install raceway on ductwork carrying particulate, corrosive fumes or flammable vapors.

Install flexible raceway sections where raceways cross expansion joints or seismic joints, where they are attached to parts of the structure with a potential for differential seismic displacement, and where they connect to equipment with designed anchors (seismic controls) or vibration isolators. Refer to Section << 26 0529 - Hangers and Supports for Electrical Systems>> and Section << 26 0548.16 - Seismic Controls for Electrical Systems>>.

For raceway systems from Trade size 1/2 through 1-1/4, install a minimum of 2 feet of flexible raceway, maximum length as determined by the <<NFPA 70>>.

For raceway systems from Trade size 1-1/2 through Trade size 2, install a minimum of 3 feet of flexible raceway, maximum length as determined by the <<NFPA 70>>.

For raceway systems larger than Trade Size 2, install a minimum of 4 feet of flexible raceway, maximum length as determined by the <<NFPA 70>>.

Use liquid-tight flexible metal conduit outdoors, in wet, damp, or corrosive indoor locations. Use flexible metal conduit in dry indoor locations. Mechanical rooms are NOT considered wet locations unless expressly indicated on the design drawings.

Install pull boxes as required to comply with the limits on raceway bends and distance between pull points in the Article << 3.4; or  _______>> Raceway Installation article of this Section; count each flexible conduit section described in this article as not less than a 90-degree bend.

Connection to vibrating equipment (including hydraulic, pneumatic, or electric solenoid or motor driven equipment). Duct work is not considered vibrating equipment. - Use a minimum of 24 inches; maximum length as determined by the <<NFPA 70>>:

          - **********************************************************************

          - The following subparagraphs are designer-choice based on environmental conditions.

          - **********************************************************************

Outdoors: Use liquid-tight flexible metal conduit.

Wet, damp, or corrosive indoor locations: Use liquid-tight flexible metal conduit. Mechanical rooms are NOT considered wet locations unless expressly indicated on the design drawings.

Dry indoor locations: Use flexible metal conduit.

Conceal raceways, unless otherwise indicated on the Drawings, with finished walls, floors and ceilings. Unless otherwise indicated on the Drawings, install concealed raceways with a minimum of bends in the shortest practical distance considering the type of building construction and obstructions.

      - ***************************************************************************************

      - The following paragraph is a designer-choice and applies to expansion fittings.

      - ***************************************************************************************

Install expansion fittings where embedded raceways cross building expansion joints.

Use raceway hubs to fasten raceway to boxes in damp and wet locations.

      - ***************************************************************************************

      - The following paragraph is a designer-choice and applies to insulating bushings.

      - ***************************************************************************************

Install insulating bushings or connectors with an insulated throat to protect conductors or cables at raceway terminations.

Install raceways with the following limits of bends and distance between pull points

Less than 50 ft, follow the <<NFPA 70>>.

50 ft to 100 ft, a maximum of 3 equivalent 90-degree bends.

100 ft to 150 ft, a maximum of 2 equivalent 90-degree bends.

150 ft to 200 ft, a maximum of with 1 equivalent 90-degree bend.

Over 200 ft, a straight run with no bend.

Stub-Up Connections

Extend raceways through concrete floor for connection to freestanding equipment with an adjustable top or coupling threaded inside for plugs, and set flush with the finished floor or equipment pad.

Extend conductors to equipment with rigid steel conduit; flexible metal conduit may be used 6 inches above the floor.

Where equipment connections are not made under this Subcontract, install threaded insert plugs set flush with the floor.

      - ***************************************************************************************

      - Retain the following Article when firestopping is required for project.

      - ***************************************************************************************

FIRESTOPPING

Install an NRTL approved firestop system at each electrical penetration in a fire-rated wall, floor, or partition.

Refer to Section << 07 8400 - Firestopping>> for materials and installation requirements.

OUTLET BOX INSTALLATION

Install outlet boxes with centers at the following heights unless noted otherwise on the Drawings:

Thermostat and zone sensor outlets:

Where user adjustable interfaces or displays are present on the device mount at 48 inches above finished floor.

          - **********************************************************************

          - The following subparagraph is a designer-choice based on the function of the interface or display.

          - **********************************************************************

Where no adjustable interfaces or displays are present on the device mount at 54 inches above finished floor.

PULL AND JUNCTION BOX INSTALLATION

Install pull and junction boxes as shown on the Drawings and as required for splices, taps, wire pulling, and compliance with regulatory requirements.

Install pull boxes as required to comply with limits on raceway bends and distance between pull points in the Article << 3.4; or  _______>> Raceway Installation article of this Section.

Install indoor pull and junction boxes in accessible locations above accessible ceilings and in unfinished spaces. Position boxes so covers can be removed. Place boxes to maintain headroom.

WIREWAY INSTALLATION

Install wireways at locations indicated on the Drawings.

Mount plumb and level.

SURFACE METAL RACEWAY INSTALLATION

Install surface metal raceway at locations indicated on the Drawings or where existing conditions make it impracticable to install in concealed spaces (i.e. block wall construction, pored wall construction).

Use flat-head screws, clips, and straps to fasten raceway channel to surfaces.

Mount plumb and level.

FIELD QUALITY CONTROL

Provide final protection and maintain conditions to ensure that coatings and finishes are without damage or deterioration at final inspection.

Inspection Points –Subcontractor to provide not less than 2 working days advance notice to the LANL STR for the following LANL inspection points and Authority Having Jurisdiction (AHJ) rough-in inspections. In the notice identify the particular areas of the Project for which LANL inspection is requested. Correct deficiencies identified during inspections.

        - ******************************************************************************

        - The following subparagraphs are designer-choice. Designer should select which environment the Raceways will be installed in and the resulting requirements.

        - ******************************************************************************

Underground raceways: After raceways have been installed but before concrete-placement or trench backfilling commences. LANL inspection may include but is not limited to

Correct raceway material and size,

Proper raceway spacing and supports,

Correct raceway stub-up locations.

Raceway connection and coupling integrity

Raceway systems in concrete walls, floors, slabs, and equipment pads: After raceways and boxes have been installed but before concrete placement commences. LANL inspection may include but is not limited to

Correct raceway system materials and sizes,

Proper raceway spacing and supports,

Raceway system connection integrity,

Correct raceway stub-up locations.

Correct outlet box locations.

Raceway systems in drywall partitions: After raceways and boxes have been installed but before drywall installation that would cover the raceway system commences. LANL inspection may include but is not limited to

Correct raceway system materials and sizes,

Proper supports for raceways and boxes,

Raceway system connection integrity,

Correct outlet box locations and proper depth setting.

Raceway systems above ceilings: After raceways and boxes have been installed but before ceiling system installation commences. LANL inspection may include but is not limited to

Correct raceway system materials and sizes,

Proper supports for raceways and boxes,

Raceway system connection integrity,

Correct outlet box locations and proper depth setting.

Firestop installation: Refer to Section << 07 8400 - Firestopping>> for required installation and proper inspection notification procedures.

CLEANING AND REPAIR

Clean interior of boxes to remove dust, debris, and other material.

Repair damage to galvanized finishes with zinc-rich paint recommended by manufacturer.

Repair damage to paint finishes with matching touch-up coating recommended by the manufacturer.

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 25 0533, REV. 2, DATED APRIL 15, 2026.