Section 26 4100 
Facility Lightning Protection

  - ************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 6 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., SECTION INCLUDES in PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Electrical POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable Sections from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality Sections.

  - ************************************************************************************************************

PART 1 GENERAL

SECTION INCLUDES

Provide lightning protection system including the following:

        - ******************************************************************************

        - Retain the following subparagraphs, depending on the scope of the project.  Grounding and bonding is always required, along with the corresponding paragraphs in PART 2.

        - ******************************************************************************

Integral strike termination device system to protect the structure.

Lightning conductors.  (e.g. Roof Conductors, Main Conductors, Down Conductors, Bonding Conductors)

Grounding and bonding for lightning protection.

Lightning protection grounding electrode system.  This includes the Loop Conductor (ground ring around building)

Surge protective devices on all conductors entering the structure.

related requirements

Section << 01 2500 - Substitution Procedures>>

Section << 26 4300 - Surge Protective Devices>>

Reference standards

ANSI C135.30 - Zinc-Coated Ferrous Ground Rods for Overhead or Underground Line Construction.

ASTM B8 - Standard Specification for Concentric-Lay-Stranded Copper Conductors, Hard, Medium-Hard, or Soft.

IEEE 837 - Qualifying Permanent Connections Used in Substation Grounding.

LPI-175 - Standard for the Design - Installation - Inspection of Lightning Protection Systems.

NECA 1 - Standard for Good Workmanship in Electrical Construction.

NFPA 70 - National Electrical Code.

NFPA 780 - Standard for the Installation of Lightning Protection Systems.

UL 96 - Lightning Protection Components.

UL 96A - Standard for Installation Requirements for Lightning Protection Systems.

UL 486A-486B - Wire Connectors.

LANL PERFORMED WORK

LANL will inspect the lightning protection system for acceptance.

SUBMITTALS

      - ***************************************************************************************

      - Submit the following per Section << 01 3300 - Submittal Procedures>>.

      - ***************************************************************************************

Action Submittals:

Catalog data for each component of the lightning protection system, including data substantiating that material complies with specified requirements.  Include data for roof adhesive when used.

QUALITY ASSURANCE

Engage a qualified installer to provide the lightning protection system.  Installer shall have either a current LPI Master Installer certification or current UL listing (Category OWAY) for Lightning Protection Installation.  The installer shall have completed not less than 5 lightning protection installations of similar scope to this Project.

LANL will inspect the lightning protection system for acceptance in accordance with contract documents and <<NFPA 780>>.

Provide products that are NRTL listed to <<UL 96>> for lightning protection use.

SEQUENCING AND SCHEDULING

Coordinate installation of lightning protection system with the installation of other building systems and components, including electrical wiring, supporting structures, building materials, and metal bodies requiring bonding to lightning protection systems.

Coordinate inspections so lightning protection conductors and bonding connections will be inspected and photographically documented before being buried, encased in concrete, or concealed by other building materials.

DELIVERY, STORAGE, AND HANDLING

Receive, store, protect, and handle products according to <<NECA 1>>

Handle conductors to prevent nicking, kinking, gouging, flattening, or otherwise deforming or weakening conductor or impairing its conductivity.

PART 2 - PRODUCTS

    - **********************************************************************************************

      - Retain the following Article if substitutions are allowed

    - **********************************************************************************************

PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted, follow Section << 01 2500 - Substitution Procedures>>.

PERFORMANCE REQUIREMENTS

Protect the entire building including roof projections, chimneys, roof-mounted equipment, associated exposed structures, electrical services, antennas, alarm services, and telecommunications services.

Provide lightning protection system that meets:

<<NFPA 780>>.  For additional information see:

<<UL 96A>>​

Lightning Protection Institute <<LPI-175>>​

Provide a system based on a 150 ft. radius rolling sphere distance as defined in <<NFPA 780>>.

Provide a lightning ground ring electrode (LGRE) that is separate from the building electrical grounding electrode system; LGRE shall be a minimum of 5 feet from the perimeter of the building and connected to the electrical grounding electrode system at a single point, outside the building.

LIGHTNING PROTECTION Material–GENERAL

Provide lightning protection materials and components that conform to<<NFPA 780>> and <<UL 96>>​

Provide lightning protection materials that are galvanically compatible with each other and with surfaces on which they are mounted or which they contact.  In general use aluminum conductors and fittings. Use copper conductors and fittings where required for galvanic compatibility or as specified on the design drawings.

Metals acceptable for contact with copper include copper, nickel, brass, tin, lead, stainless steel, and Monel TM.

Metals acceptable for contact with aluminum include aluminum, magnesium, zinc, galvanized steel, stainless steel, lead, and wrought iron.

Provide conductors with protective coatings or oversize conductors where unusual conditions exist which would cause corrosion of conductors.

Provide lightning protection materials that are protected against deterioration due to corrosive environments at the local point of installation.

Local points of installation where corrosive environments may exist are, but not limited to, the top of a chimney or vent emitting corrosive gases, or the top of heavy duty stacks.

Hot-dipped lead coated materials are not permitted without prior permission of the LANL AHJ.

      - ***************************************************************************************

      - Retain the following paragraph if existing material will be reused.

      - ***************************************************************************************

Existing lightning protection material and components that meet the requirements of this Section and are in good condition visually may be re-conditioned and re-used.  Re-conditioning includes removal of adhesive, removal of corrosion, and wire brushing contact areas.

System Materials

      - ***************************************************************************************

      - The following paragraph will be automatically activated when "strike termination devices" is activated in Part 1.  Retain the appropriate materials in the subparagraphs to match the project conditions. Care should be taken if specifying copper strike termination devices. Copper devices should not be connected to aluminum conductors due to corrosion, especially from rain runoff. Aluminum components should not be used where embedded in concrete or masonry, or attached to a surface coated with alkali-based paint.

      - ***************************************************************************************

Strike Termination Devices:

Copper: Provide 1/2 inch-diameter, rounded-tip, solid-copper strike-termination devices.

Aluminum: Provide 5/8 inch-diameter, rounded-tip, solid-aluminum strike-termination devices.

Strike-termination device tips shall have a tip radius of curvature of from 3/16 inch to 1/2 inch.

Provide a cast base for each strike-termination device that matches the device material, has a bolted, pressure-type cable connector, will support the terminal in a vertical position, and is suitable for the surface to which it will be attached.

      - ***************************************************************************************

      - The following paragraph is automatically activated when "lightning conductors" is activated in Part 1. Retain the appropriate subparagraphs per the project requirements.

      - ***************************************************************************************

Conductors:

Copper Main Conductor: Provide copper cable with minimum 17 AWG strand size and a minimum cross-sectional area of 57,400 circular mils.

Aluminum Main Conductor: Provide aluminum cable with minimum 14 AWG strand size and a minimum cross-sectional area of 98,600 circular mils.

Copper Bonding Conductor: Provide copper cable with minimum 17 AWG strand size and a minimum cross-sectional area of 26,240 circular mils.

Aluminum Bonding Conductor: Provide aluminum cable with minimum 14 AWG strand size and a minimum cross-sectional area of 41,100 circular mils.

Provide bolted pressure type connectors. Finger, crimp, or pressure saddle style cable connectors are not acceptable.

      - ***************************************************************************************

      - The following two paragraphs are automatically activated when "strike termination devices" is activated in Part 1.

      - ***************************************************************************************

For installations on standing seam metal roofs provide strike termination device bases and cable fasteners that clamp to the standing seams and are compatible with the roofing system and the lightning protection system materials.

Provide cast swivel couplings, as required, to install strike termination devices vertically.

      - ***************************************************************************************

      - Retain the following paragraph if strike termination devices will be installed on membrane roofing.  Retain the appropriate subparagraphs.

      - ***************************************************************************************

For installations on membrane roofing or other surfaces that must not be penetrated provide attachments for strike termination device bases and cable fasteners by one of the following:

Provide adhesives for cable fasteners and strike termination device bases that are compatible with surface or roofing material to which bases or fasteners are to be attached.

Provide bases and fasteners that will stay in position and prevent overturning by using gravity or mechanical attachment.

Manufacturers: East Coast Lightning Equipment, Harger Lightning Protection, Thompson Lightning Protection.

      - ***************************************************************************************

      - The following Article is automatically activated when "lightning Protection grounding electrode system" is activated in part 1.

      - ***************************************************************************************

GROUNDing System Material

      - ***************************************************************************************

      - Retain either "Ground Rods" or "Ground Ring" or both, as appropriate. A ring is the preferred method.

      - ***************************************************************************************

Ground Rods:

Provide ground rods as shown on the Drawings.

Furnish ground rods that comply with <<ANSI C135.30>> with high-strength steel core and electrolytic-grade copper outer sheath, molten-welded to core, approximately 10 feet long, 3/4-inch diameter.

Manufacturers: Blackburn, Thomas & Betts, Harger

Ground Conductor–Ring:

Provide bare-stranded, soft-temper copper conductor that conforms to <<ASTM B8>>​

Provide conductor size as indicated on the Drawings or specified in this Section, 1/0 AWG minimum.

      - ***************************************************************************************

      - The following article is automatically activated when "lightning protection grounding electrode system is activated in Part 1.  Retain the subparagraphs as is appropriate for the project.

      - ***************************************************************************************

Grounding Connectors

Bolted Ground Connectors:

Provide NRTL-listed, copper-alloy, bolted connectors with silicon-bronze hardware for making cable connections to pipes, ground rods, exposed structural steel, roof deck, and wall panels.

Manufacturers:  Blackburn, Burndy, O.Z.

Exothermic-Weld Connections:

Provide molds and welding material in kit form for making exothermic weld connections.

Match mold and weld material to material types, shapes and sizes to be joined.

Manufacturer:  ERICO Cadweld

Compression Grounding Connectors:

Provide NRTL-listed, wrought-copper connectors, terminals, and splices for making compression grounding connections on concentric lay ground electrode cable and bonding connections to reinforcing steel.

Furnish connectors that have been tested successfully according to the requirements of <<IEEE 837>>​.

Provide hydraulic compression tools and dies that match the connectors.

Match connector and die size to material shapes and sizes to be joined.

Manufacturer: Blackburn, Burndy

PART 3 - EXECUTION

    - **********************************************************************************************

      - Retain the following Article if existing work is in the scope of the project.

    - **********************************************************************************************

EXISTING WORK

Existing lightning protection material and components that meet the requirements of this Section and are in good condition may be re-conditioned and re-used.  Re-conditioning includes removal of adhesive, removal of corrosion, and wire-brushing contact areas.

Inspect, and repair the parts of the existing lightning protection system on the structure that are to remain in service.

Perform continuity tests to verify that the lightning grounding electrode system is connected to the electrical system grounding electrode system.

Visually inspect existing surge suppression devices on electrical equipment, electrical circuits, and communications, alarm, control, and antenna systems for indication of damage.  Notify the STR of any missing or damaged surge suppression devices.

EXAMINATION

Examine surfaces and conditions, with Installer present, for compliance with installation tolerances and other conditions affecting performance of the lightning protection system.  Do not proceed with installation until unsatisfactory conditions have been corrected.

INSTALLATION–General

Install lightning protection system according to <<NFPA 70>> and <<NFPA 780>> , as specified in this Section, and as shown on the Drawings.

Install lightning protection components according to manufacturer's written instructions.

      - ***************************************************************************************

      - The following paragraph is automatically activated when "strike termination devices" is activated in Part 1.

      - ***************************************************************************************

Install strike termination devices on ridges, parapets, and around the perimeter of buildings with flat roofs at spacing as shown on the drawings. Install supplemental strike termination devices as required by <<NFPA 780>>. Permanently and rigidly attach strike termination devices to prevent overturning. Install swivel adapters as required to position strike termination devices vertically.

On standing-seam metal roofs, use attachments for strike-termination device bases and cable fasteners that clamp to the standing seams.

On membrane roofing or other surfaces that must not be penetrated, attach strike-termination device bases and cable fasteners using materials and methods that, preferably, do not depend on adhesive alone for proper performance.  Coordinate with roofing material installer.

Acceptable installation methods on membrane roofs include:

Mechanical fastening to nailer blocks that are pre-installed by the roofing Subcontractor. Coordinate locations with the roofing subcontractor.

Approved top-fill ballast pans (6-inch diameter for strike-termination devices and 3-inch diameter for cable fasteners) that are filled with structural-density concrete then attached with adhesive to the membrane roof.

Use adhesives that are recommended by manufacturer of the cable fasteners and strike termination device bases and are approved by manufacturer of the roofing material.  Prepare roof surface and apply adhesives according to manufacturer's instructions.

Install roof conductors so they will be visible for inspection and testing.

Install down-conductors at locations compatible with the building structure and architectural design with consideration given to the location of ground connections.

Course exposed down-conductors over the extreme outer portions of the exterior of the building, such as corners.

Install an accessible down-conductor disconnect in each down-conductor except the one nearest the building electrical service; use 4-bolt tubular splice fittings.

Cover down-conductors that are subject to physical damage or displacement with Schedule 80 PVC conduit.  Cover down-conductors from grade level up to 6 ft. above grade.  Support conduit with conduit clamps spaced not more than 36 inches apart.

      - ***************************************************************************************

      - The following Article is automatically activated by the associated paragraph in Part 1.

      - ***************************************************************************************

LIGHTNING PROTECTION GROUNDING ELECTRODE SYSTEM

Ground ring Electrode (Loop Conductor): Install a ground ring around the building or structure.  Use minimum 1/0 AWG ground conductor located 5 ft. outside the building perimeter and at least 6 ft. from any electrical system or communications system grounding.  Install the ground ring at least 3 ft. below grade.

Other Made Electrodes: Where it is not possible to install a ground ring as the lightning protection grounding electrode, or the ground ring must be supplemented, install one or more made grounding electrodes located 5 ft. outside the building perimeter and at least 6ft from any electrical system.

Connect the lightning grounding electrode system to the electrical system at a location that is outside the building in a manner where the connection can be inspected and accessible for testing and will not be subject to damage.

LIGHTNING PROTECTION CONNECTIONS

Clean contact surfaces to which lightning protection connections are to be made.  Remove non-conductive coatings such as paint, enamel, and oil film.  Install connectors according to their listing.

Use the following connection methods:

Use bolted connectors for connecting to ground rods.

Use exothermic weld connections for underground or concealed connections of dissimilar materials.

Use exothermic weld or compression grounding connections for underground or concealed connections of like materials.  Do not use compression grounding connectors for rope lay lightning conductor connections or for lightning protection ground rod connections.

Use exothermic weld or bolted connections for accessible connections.

Use high strength silicon bronze bolts, nuts, flat washers and toothed lock washers for making bolted connections.

Tighten lightning protection connectors, screws and bolts in accordance with manufacturer's published torque tightening values for connectors and bolts. Where manufacturer's torquing requirements are not indicated, tighten connections to comply with <<UL 486A-486B>>. Use a calibrated torque wrench.

Use hydraulic compression tools to provide the correct circumferential pressure for compression connectors.  Use tools and dies recommended by the manufacturer of the connectors.  Provide embossing die code or other standard method to make a visible indication that a connector has been adequately compressed.

Install exothermic welds in accordance with manufacturer's instructions and recommendations.  Welds that are puffed up or that show convex surfaces indicating improper cleaning are not acceptable.

Make connections in such a manner as to minimize possibility of galvanic action or electrolysis.  Select connectors, connection hardware, conductors, and connection methods so metals in direct contact will be galvanically compatible.

Use electroplated or hot-tin-coated materials to assure high conductivity and make contact points closer in order of galvanic series.

Make connections with clean bare metal at points of contact.

Make aluminum to steel connections with stainless steel separators and mechanical clamps.

Make aluminum to galvanized steel connections with tin-plated copper jumpers and mechanical clamps.

Coat and seal connections involving dissimilar metals with inert material to prevent future penetration of moisture to contact surfaces.

Protect lightning protection connections to prevent them from being painted or covered with material such as fire proofing or roofing adhesive.

      - ***************************************************************************************

      - The following Article is automatically activated when "surge protective devices" is activated in Part 1.

      - ***************************************************************************************

SURGE Protective Devices

Refer to Section << 26 4300 - Surge Protective Devices>>.

Verify and document the location of installed surge protective devices.

FIELD QUALITY CONTROL

Inspect the lightning protection system to determine:

That the system complies with the current <<NFPA 780>>.

That all required bonds are in place and are secure.

That the AC power lines, communications, and data lines that enter the facility, as described in <<NFPA 780>>, have surge suppression devices that are properly installed.

Take corrective action to correct deficiencies.  Provide certified inspection and test results and instrument specifications and calibration information to the LANL STR.

An inspection of the lightning protection system will be conducted by a LANL-approved lightning protection system inspector prior to system acceptance.

Notify the LANL STR 10 working days in advance of the expected completion of the lightning protection system installation.  Inspection can be scheduled in parts or by area depending on the system and construction schedule.

Promptly correct all deficiencies as required by the LANL STR.

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 26 4100, REV. 6, DATED APRIL 15, 2026.