Section 26 4300 
Surge Protective Devices

  - ************************************************************************************************

    - LANL MASTER SPECIFICATION section

Rev. 3 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., SECTION INCLUDES in PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Electrical POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable sections from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects. For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality Sections.

      - ==========================================================

      - This revision is to correlate with UL 1449, 4th Edition and Article 242 in NFPA 70.

      - Type 1 SPDs are designed to be used on the line side of a service disconnect, directly connected to the transformer secondary conductors.  They may also be used on the load side.

      - Type 2 SPDs are designed to be used on the load side of a circuit breaker.

    - **********************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

      - ***************************************************************************************

      - This Section is written for Type 1 SPDs.  Type 1 SPDs may be installed on the line or the load side of the service.  Type 2 SPDs are acceptable to LANL.  If Type 2 SPDs are used, do not issue this Section.  Use supplier standard.  If Type 2 SPDs are used for explosive facilities, place in the notes on the drawings that they must comply with the requirements of NFPA 780.

      - ***************************************************************************************

General requirements for type 1 surge protective devices (SPDs) for the protection of electrical power circuits not exceeding 1000 V.

Type 1 surge protective devices (SPD’s) for the protection of electrical power circuits not exceeding 1000 V.

      - ***************************************************************************************

      - This following is a designer choice, if SPDs are required for signal, data, antenna, or control lines.  If the service provider of these lines has provided surge protection, there is no need to provide additional surge protection.

      - ***************************************************************************************

SPDs for the protection of signal, data, antenna, and control lines.

related requirements

Section << 01 2500 - Substitution Procedures>>

Section << 01 3300 - Submittal Procedures>>

reference standards

NECA 1 - Standard for Good Workmanship in Electrical Construction.

NFPA 70 - National Electrical Code.

NFPA 780 - Standard for the Installation of Lightning Protection Systems.

UL 497B - Standard for Protectors for Data Communications and Fire-Alarm Circuits.

UL 497C - Protectors for Coaxial Communications Circuits.

UL 1449 - Standard for Surge Protective Devices.

ACTION SUBMITTALS

Submit the following per Section << 01 3300 - Submittal Procedures>>:

Catalog Data: Submit catalog data describing SPDs. Include data substantiating that proposed products comply with specified requirements.

Installation Instructions: Manufacturer’s manual.

QUALITY ASSURANCE

Comply with <<NFPA 70>> and <<NFPA 780>>.

Provide SPDs that are listed by a Nationally Recognized Testing Laboratory (NRTL). Listing standard shall be the following, as applicable:

<<UL 1449>>​​

<<UL 497B>>​​

<<UL 497C>>​

Provide SPDs suitable for use at a nominal altitude of 7500 ft.

DELIVERY, STORAGE, AND HANDLING

Receive, store, protect, and handle products according to the manufacturer’s instructions and <<NECA 1>>.

PART 2 - PRODUCTS

    - **********************************************************************************************

      - Retain the following article if substitutions are allowed on the Project.

    - **********************************************************************************************

PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section << 01 2500 - Substitution Procedures>>.

general spd requirements for power applications

NRTL listed to <<UL 1449>>​.

SPD shall provide surge current paths for at least the following modes of protection:

L-N, L-G, and N-G for wye-connected systems and single-phase systems.

L-L, L-G in delta-connected systems.

Provide each individual SPD intended for mounting external to the electrical assembly with a NEMA enclosure suitable for the installation location and environment, as indicated on drawings.

NEMA 1, 12, 3R, and 4 enclosures: powder-coated steel.

NEMA 4X enclosures: polycarbonate or Type 304 stainless steel.

Type 1 SPD

AC Power SPDs shall have a <<UL 1449>> Short Circuit Current Rating (SCCR) not less than the following:

| System Voltage | Circuit Size | Minimum SCCR |
| --- | --- | --- |
| 480Y/277 | Any | 200 kA |
| 480 Delta | Any | 200 kA |
| 208Y/120 | Greater than 400 A | 200 kA |
| 208Y/120 | 400 A and less | 100 kA |
| 120/240 | Any | 100 kA |

SPD shall be suitable for use without external or supplemental overcurrent protection. Every suppression component of every mode shall be protected by internal overcurrent and thermal over-temperature controls. SPDs relying upon external or supplementary overcurrent protection will not be considered.

SPD shall have a UL 1449 nominal discharge current rating (In) of not less than 20 kA.

Suppression components shall be thermally-protected 32 mm or larger metal-oxide varistors (MOVs).

AC Power SPDs minimum surge current capability (single pulse rated) per phase shall be as indicated for the following applications:

Service Equipment or Transfer Switch:

| System Voltage | Equipment Size | Minimum Surge Current Capability |
| --- | --- | --- |
| 480Y/277 | Any | 240 kA |
| 480 (ungrounded) | Any | 240 kA |
| 208Y/120 | Greater than 400 A | 240 kA |
| 208Y/120 | 400 A and less | 100 kA |
| 120/240 | Any | 100 kA |

Panelboards and MCCs that supply one or more electrical circuits that leave the structure to supply another structure and the conductors extend more than 100 feet:

| System Voltage | Minimum Surge Current Capability |
| --- | --- |
| 480Y/277 | 150 kA |
| 480 (ungrounded) | 150 kA |
| 208Y/120 | 100 kA |
| 120/240 | 100 kA |

Panelboards and MCCs that supply one or more electrical circuits that leave the structure to supply equipment that is exposed to lightning (e.g. roof mounted HVAC equipment, parking lot lighting):

| System Voltage | Minimum Surge Current Capability |
| --- | --- |
| 480Y/277 | 150 kA |
| 480 (ungrounded) | 150 kA |
| 208Y/120 | 100 kA |
| 120/240 | 100 kA |

AC Power SPDs <<UL 1449>> Voltage Protection Rating (VPR) shall not exceed the following:

| System Voltage | L-N | L-G | L-L | N-G |
| --- | --- | --- | --- | --- |
| 480Y/277 | 1200V | 1200V | 2000V | 1200V |
| 480 (ungrounded) | --- | 1800V | 2000V | --- |
| 208Y/120 | 700V | 700V | 1200V | 700V |
| 120/240 | 700V | 800V | 1200V | 700V |

<<UL 1449>>​ Maximum Continuous Operating Voltage (MCOV) rating shall be not less than the following:

| System Voltage | Allowable System Voltage Fluctuation (%) | MCOV |
| --- | --- | --- |
| 480Y/277 | 15% | 550/320V |
| 480 (ungrounded) | 15% | 550V |
| 208Y/120 | 25% | 150V |
| 120/240 | 25% | 150V |

AC Power SPDs shall include not less than the following monitoring and diagnostic features that report the protection status of the SPD:

One green LED (protected) indicator per phase and one red (not protected) LED.

For SPDs with a surge current capacity greater than 100 kA provide an audible alarm with on/off silence function, and one set of NO/NC contacts that change state under any fault condition.

Where indicated on the Drawings or specified in other Sections, provide SPDs that are factory installed and integrated within the protected electrical equipment, .

Manufacturers:

Advanced Protection Technologies:

Surge Current Capability over 100 KA: “XAS” series.

Surge Current Capability 100 KA or less: “XDS” series.

Eaton:

Surge Current Capability over 100 KA: “SPD” series,

Surge Current Capability 100 KA or less: “CVX100” series.

Siemens:

Surge Current Capability over 100 KA: “TPS3 01,” TPS3 05”, “TPS3 06,” “TPS3 12.”

Surge Current Capability 100 KA or less: “TPS3 11.”

Square D:

Surge Current Capability over 100 KA: “IMA” and “EMA” series.

Surge Current Capability 100 KA or less: “IMA” and “EMA” series.

      - ***************************************************************************************

      - The following article is activated when the corresponding paragraph in PART 1 is activated. Retain applicable paragraphs per project requirements.

      - ***************************************************************************************

SPD FOR signal, data, Antenna, and control lines

Provide SPDs suitable for the protection of signal, data, antenna, and control lines.

Select SPDs with consideration for aspects such as the frequency, bandwidth, voltage, and current of the signal, data, antenna, or other communications lines and to ensure that insertion losses introduced by the surge protective devices are within acceptable operational limits.

Coordinate selection of SPDs for signal, data, antenna, and control lines with owner of equipment that is served by the lines.

Provide SPDs for of signal, data, and control lines that provide both common mode and differential mode protection.

Provide SPDs for signal, data, control, and alarm lines.

Provide devices with ratings and connectors as required by the application.

Manufacturer: Phoenix Contact, EDCO, MCG Electronics

Provide coaxial SPDs for antenna and RF signal lines.

Devices shall be listed in accordance with <<UL 497C>>.

Provide devices with ratings and connectors as required by the application.

Provide bulkhead plates and low-impedance paths to ground where antenna cables enter the structure.

Manufacturers: TII Network Technologies, Inc., Cable Innovations, PolyPhaser

PART 3 - EXECUTION

EXAMINATION

Verify mounting area is ready for SPDs.

Verify that circuit rough-in is at correct location.

INSTALLATION

Install SPDs as specified below, according to the manufacturer's instructions, <<NFPA 780>>, and <<NFPA 70>>. Have the manufacturer’s installation instructions available at the construction site.

      - ***************************************************************************************

      - Retain the following paragraph if SPDs are to be installed in Service Equipment.  If buildings are fed from a feeder, instead of Utility, omit this paragraph.  Retain the paragraph for Power Panelboard or MCC instead.

      - ***************************************************************************************

Service Equipment:

Install a SPD that is ​<< factory installed and integrated into; or  individually mounted immediately adjacent to>>​ each low-voltage service equipment.

Connect SPD on the ​<< line side; or  load side>>​ of the service disconnecting means.

Provide a means of connection for the SPD, as recommended by the manufacturer. This might be a sub-feed connection block, or it might be a dedicated circuit breaker.

      - ***************************************************************************************

      - Retain the following paragraph if applicable to the Project.

      - ***************************************************************************************

Automatic Transfer Switch:

Install an individual SPD mounted immediately adjacent to each automatic transfer switch that is connected to an outdoor generator.

Connect SPD on the alternate source side of the automatic transfer switch.

      - ***************************************************************************************

      - Retain the following paragraph if applicable to the project.  For Example, if a building is fed by a feeder, it is not a service.  In this case, the Service Equipment paragraph should be omitted.  Retain the appropriate subparagraphs in this paragraph to match the project conditions.

      - ***************************************************************************************

Power Panelboard or Motor Control Center:

Install a SPD that is ​<< factory installed and integrated into; or  individually mounted immediately adjacent to>>​ each power panelboard or motor control center that supplies electronic equipment (e.g. computers, adjustable frequency drives, and laboratory equipment).

Install a SPD that is ​<< factory installed and integrated into; or  individually mounted immediately adjacent to>>​ each power panelboard or motor control center that supplies one or more electrical circuits that leaves the structure to supply another structure and the conductors extend more than 100 feet.

Install a SPD that is ​<< factory installed and integrated into; or  individually mounted immediately adjacent to>>​ each power panelboard or motor control center that serves one or more electrical circuits that leaves the structure to supply equipment that is exposed to lightning (e.g. roof mounted HVAC equipment, parking lot lighting).

Provide a dedicated 3-pole circuit breaker, sized as per manufacturer’s instructions, in the panelboard or MCC as the SPD interface device.

Connect SPDs to protect each ungrounded (line) and grounded (neutral) conductor.

      - ***************************************************************************************

      - Retain the following paragraph if SPDs will be installed on signal, data, control, or alarm circuits.

      - ***************************************************************************************

Install listed SPD for each for signal, data, control, and alarm line that enters the structure or exits the structure to serve external detached equipment or other detached structures. Where such signal, data, control, and alarm circuits are longer than 100 ft. install listed SPD at both ends of the circuit.

      - ***************************************************************************************

      - Retain the following paragraph if SPDs will be installed on antenna and/or RF circuits.

      - ***************************************************************************************

Install listed coaxial SPD for each for antenna and RF signal line that enters the structure or exits the structure to serve external detached equipment or other detached structures. Where such antenna and RF signal circuits are longer than 100 ft. install listed coaxial SPD at both ends of the circuit.

Install each SPD so it will be accessible for inspection and maintenance.

Install SPDs in a manner that will not limit the use of through-feed lugs, sub-feed lugs, or sub-feeder circuit breakers in panelboards.

Install each SPD with conductor length according to the manufacturer’s instructions.

Twist conductors tightly together and keep runs as straight as possible with no sharp bends or kinks.

Field Quality Control

Provide final protection and maintain conditions to ensure that coatings and finishes are without damage or deterioration at final inspection.

Repair damage to paint finishes with matching touch-up coating recommended by the manufacturer.

Verify that each SPD is correctly connected and that all condition monitoring indicators operate properly.

Verify mechanical integrity of each conductor connection.

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 26 4300, REV. 3, DATED APRIL 15, 2026.