Section 27 1500.18 
Classified Network Infrastructure Rough-In

  - ************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 4 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., SECTION INCLUDES in PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Secure Communications POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - Section is developed for ML-4 projects. For ML-1, -2, and -3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10, Specifications and Quality sections.

      - Seismic: Template does not include such verbiage. If appropriate to include it, copy language from Section << 27 1000 - Structured Cabling>>.

  - ************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

Classified Network Infrastructure (CNI) rough-in to serve the secure communications areas in the building as indicated on the drawings. CNI system to include:

        - ******************************************************************************

        - The following subparagraphs are designer-choices. Retain subparagraphs based on project-scope.

        - ******************************************************************************

Conduit

Wireway

CNI Cable

CNI Outlet Boxes

Cross-Connect Equipment

RELATED REQUIREMENTS

Section << 01 2500 - Substitution Procedures>>

Section << 01 3300 - Submittal Procedures>>

Section << 26 0529 - Hangers and Supports for Electrical Systems>>​

Section << 27 1000 - Structured Cabling>>

Section << 33 7119 - Electrical Underground Ducts and Manholes>>

REFERENCE STANDARDS

NECA 1 - Standard for Good Workmanship in Electrical Construction.

NECA/FOA 301 - Standard for Installing and Testing Fiber Optic Cables.

NFPA 70 - National Electrical Code.

      - ***************************************************************************************

      - Retain the following Article when CNI cable and/or CNI outlet boxes are in project-scope. Retain the applicable paragraphs based on project-scope.

      - ***************************************************************************************

LANL-FURNISHED EQUIPMENT FOR SUBCONTRACTOR INSTALLATION

Fiber-optic cable required to connect CNI outlets

CNI outlet boxes

Fiber-optic backbone cables

      - ***************************************************************************************

      - Retain the following Article when CNI cable, CNI outlet boxes and/or cross-connect equipment are in project-scope. Retain the applicable paragraphs based on project-scope.

      - ***************************************************************************************

LANL-FURNISHED AND INSTALLED EQUIPMENT

CNI outlet/connectors

CNI patch panel racks

Fiber-optic entrance cable

      - ***************************************************************************************

      - Retain the following Article when conduit, wireway and/or CNI cable are in project-scope. Retain the applicable paragraphs based on project-scope.

      - ***************************************************************************************

LANL PERFORMED WORK

Perform a comprehensive visual inspection of all CNI raceways before they are covered. Coordinate inspection with the LANL Telecommunications Group Site Coordinator.

Terminate CNI cables.

Test terminated CNI cables.

COORDINATION

Verify that the CNI Security Plan has been approved by the LANL Telecommunications Group Site Coordinator before beginning work.

Schedule inspections of the CNI raceway system with the LANL Telecommunications Group and LANL Building Inspector Vice OSH before covering with building finishes. Coordinate schedule with the LANL Telecommunications Group Site Coordinator.

Schedule completion of the secure telecommunications (server) rooms to allow no less than 5 working days for the LANL Telecommunications Group to install CNI patch panel racks before the scheduled start of cable installation. Coordinate schedule with the LANL Telecommunications Group.

Request CNI outlet boxes and fiber-optic cable from the LANL Telecommunications Group based on actual count, measurement of conduit and wireway runs and required slack cable. Place order at least 10 working days prior to scheduled start of cable installation.

Schedule installation of surface-mounted CNI outlet boxes and associated surface mounted conduit to start after the completion of application of finishes to walls.

Schedule installation of CNI cabling to start after structural inspection and the completion of application of finishes to walls to minimize potential damage to cables. Cabling is to be installed per manufacturer’s instructions regarding minimum temperature requirements. The project is responsible to meet these requirements

ACTION SUBMITTALS

Submit the following in accordance with Section << 01 3300 - Submittal Procedures>>.

Within 30 days after Notice to Proceed, submit certifications of the qualifications of the fiber-optic cable installers, as described in Article ​<< 1.10; or  _______>>​ Quality Assurance of this Section, to the LANL Telecommunications Group (ISD-TS) for review and approval before work can commence.

Provide Fluke LinkWare test results in electronic file format for each cable to the LANL Telecommunications Group for review and acceptance.

INFORMATIONAL SUBMITTALS AT CLOSEOUT

At the conclusion of physical work, provide detailed Project record documents (PRDs) showing outlets, routing, and size of raceways, junction boxes, and pull boxes to the LANL Subcontract Technical Representative (STR). The LANL Requesting Organization will then submit the PRDs (along with an Enclosure 2, Classified Network Infrastructure Security Plan) to the LANL Telecommunications Group POC.

QUALITY ASSURANCE

Comply with the <<NFPA 70>> (NEC) for components and installation.

Provide products that are listed and labeled by a Nationally Recognized Testing Laboratory (NRTL) for the application and environment in which installed.

Conform to the LANL CNI Master Plan.

Qualifications of copper and fiber-optic cable installers:

Category 6A horizontal cables: BICSI Registered Installer Level 2 or equivalent certification plus successful completion of Systimax Installer Training that includes installation and termination of Category 6A cable; experience installing and terminating Category 6A cables on at least two previous projects.

Fiber optic horizontal cables, all backbone cables: BICSI Registered Installer Level 2 or equivalent certification; experience installing backbone and fiber optic cables on at least two previous projects.

Copper and fiber installers shall have Fluke copper and fiber testing certification.

Recognized manufacturers, distributors, and industry certifiers include Corning, Belden, Systimax, and BICSI.

Security clearance requirements:

With approval from LANL Telecommunications Group Site Coordinator, UNCLEARED personnel may perform the following CNI system work in new buildings: mounting protective outlet boxes (POBs), placing conduit, and pulling fiber cable.

Structure must be placed by NM-EE98J licensed electricians.

UNCLEARED personnel must be accompanied by escorts if work is in a Security Area.

CNI fiber termination and testing will be performed by LANL Q-CLEARED personnel only.

If the fiber cable is placed by UNCLEARED personnel, additional testing MUST be performed: The fiber must be Optical Time Domain Reflectometer (OTDR)-tested twice, once from each end of the fiber cable, and at each wavelength. Using UNCLEARED installation personnel will result in higher costs to the project for testing.

DELIVERY, STORAGE, AND HANDLING

Receive, transport, store, protect, and handle products according to <<NECA 1>> and <<NECA/FOA 301>>.

Transport LANL-furnished material and equipment to the jobsite.

PART 2 - PRODUCTS

    - **********************************************************************************************

      - The following Article Product Options and Substitutions is a designer-choice Retain when project allows for substitutions.

    - **********************************************************************************************

PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section << 01 2500 - Substitution Procedures>>.

      - ***************************************************************************************

      - Retain the following Articles Conduit, Wireway, CNI Cable, CNI Outlet Boxes and/or Cross-Connect Equipment  based on project-scope.

      - ***************************************************************************************

CONDUIT

Use intermediate metal conduit (IMC) with threaded fittings in concealed areas that are not visually accessible. Use electrical metallic tubing (EMT) or plastic wireway only where approved by LANL Telecommunications Group Site Coordinator.

Minimum conduit size: 1 inch

Refer to Section << 27 1000 - Structured Cabling>>.

WIREWAY

Manufacturer: Square D “Square-Duct”.

Provide NRTL-listed lay-in wireway, complete with hinged covers, elbows, tees, hangers, and fittings required for a complete system.

NRTL listing shall include use as equipment grounding conductor.

Elbow, tee, and cross fittings shall be fabricated with 45 degree segments to accommodate bending radii for fiber optic cables.

Supply wireway without knockouts, wing nuts, or clips. Fasten covers securely with screws.

Supply wireway with inside and outside gray polyester powder finish over a phosphate surface preparation.

For CNI wireway that is not exposed (above the ceiling or underneath the floor), supply tamper-resistant fasteners for assembling the wireway and for securing covers.

Use button-head “Torx” tamper-resistant cap screws with a solid post in the center.

Use conical “Trident” tamper-resistant nuts, where located on the outside of the wireway.

CNI CABLE

Cable consists of multiple fibers; cable outside diameter is approximately 0.25 inches.

CNI OUTLET BOXES (LANL-FURNISHED)

LANL Telecommunications Group Site Coordinator will determine specifications of protective outlet boxes (POBs) and authenticated outlet boxes (AOB) to be used on a case-by-case basis.

POBs and AOBs are metal, surface-mounted, 10 x 6.5 x 3.5 inches boxes with a lockable, welded-hinged cover.

CROSS-CONNECT EQUIPMENT (LANL-FURNISHED)

Cross-connect equipment for CNI fiber-optic cables will consist of patch panel racks.

Fiber optic terminations will be made by LANL.

PART 3 - EXECUTION

    - **********************************************************************************************

      - Retain the following Article when existing construction is affected.

    - **********************************************************************************************

EXISTING WORK

When a requirement no longer exists for a CNI, the user will prepare and submit a Request to the LANL Telecommunications Group POC and the LANL Telecommunications Group Site Coordinator requesting termination of support.

Identify, tag, and remove exposed abandoned CNI system components, including abandoned cable and raceways and markings above accessible ceiling finish back to source. Patch surfaces where removed cables pass through building finishes.

Only U.S. Government cleared, technically competent personnel may install, modify, or maintain any portion of an active LANL CNI.

Do not leave active CNI open and unsupervised during modifications. DO NOT keep keys overnight; at the end of each day all keys must be returned and checked in.

For existing CNI systems, or for new systems that have been locked, check out and sign for keys daily.

For customer owned CNI systems, the CNI owner will supply keys.

For LANL Telecommunications Group owned systems, keys will be supplied by the LANL Telecommunications Contracts Management.

Extend existing CNI using materials and methods as specified herein.

EXAMINATION

Verify interior of building has been protected from weather.

Verify that work of other trades likely to damage CNI components has been completed.

Examine building finishes that are to receive CNI components and cables for compliance with installation tolerances and other conditions. Do not proceed with installation until unsatisfactory conditions have been corrected.

CNI device locations and raceway routings shown on Drawings are approximate unless dimensioned.

CNI components as required to meet project conditions.

Route raceways and cables as required to meet project conditions.

Where raceway routing is not shown, and destination only is indicated, determine exact routing and lengths required to meet project conditions. Record actual routing on as-built drawings.

CNI GENERAL INSTALLATION REQUIREMENTS

Verify that CNI Security Plan has been approved by the LANL Telecommunications Group Site Coordinator before beginning any CNI system installation.

Install CNI in accordance with the LANL CNI Master Plan. Installation requirement information in these documents is available from the LANL Telecommunications Group Site Coordinator.

      - ***************************************************************************************

      - Retain the following Articles Conduit installation, Wireway Installation, CNI Cable Installation and/or CNI Outlet Installation based on project-scope.

      - ***************************************************************************************

CONDUIT INSTALLATION

Install CNI service entrance conduits.

Refer to Section ​<< 33 7119 - Electrical Underground Ducts and Manholes>>​, for description. Also refer to LANL ESM Chapter 19 - Communications, Section G50, Site Communications.

Turn up the secure telecommunications conduits in the main secure telecommunications (server) room in a 24 x 24 x 12 inches, hinged-cover box or as directed by LANL Telecommunications Group.

Provide a woven polyester pull tape (1200 lb. test) with stamped footage markings into each service conduit and tied off at each end.

Install an individual 1-inch conduit for CNI cable from each CNI outlet box to the CNI wireway.  Currently up to 11, 6-strand fibers are being placed in a 1-inch conduit.

Install CNI conduits that will contain only fiber-optic cables so they will have 2 inches of separation from other utilities throughout the conduit route.

Acoustical Ceilings: Conduits above accessible ceilings are only allowed with LANL Telecommunications Group permission and direction. When allowed, this is typically required to be 3 inches above the ceiling tiles and below suspended mechanical equipment, piping, ductwork, cable trays, and building structure so entire route is visible for inspection.

CNI conduits passing through walls, floors, and ceilings shall have no hidden joints or fittings. Firestop material must not cover pipe threads; they must be visible.

Surface mount CNI conduits and outlets in offices so they will be visually inspectable.

Provide a woven polyester pull tape (1,200 lb test) with stamped footage markings in each empty CNI conduit. Do not leave any pull strings hanging out of the CNI anywhere.

Use bends on conduits for horizontal cables with a minimum inner edge radius of 5 inches.

Do not use conduit bodies for changes in direction or as pull boxes.

WIREWAY INSTALLATION

Install CNI wireway following the manufacturer’s installation instructions and <<NECA 1>>. Manufacturer’s installation instructions must be available at the work site.

Use CNI wireway only in corridors, secure telecommunications rooms, secure server rooms, and vault-type rooms.

If permitted by the CNI Security Plan, CNI wireway may be installed above corridor suspended accessible ceiling.

Install CNI wireways with not less than 12 inches access above and 12 inches to one side of each wireway to permit access for installing and maintaining cables and for security inspections.

Bond each section of the wireway to ensure electrical continuity. Bond the wireway to the secure telecommunications (server) room ground bar with 6 AWG copper conductor.

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements.

      - ***************************************************************************************

Extend CNI wireways to patch panel racks in the << secure server room(s);  secure telecommunications room(s); or  vault-type room(s)>>​. Coordinate attachments to racks with LANL Telecommunications Group.

Support and brace wireway in accordance with Section << 26 0529 - Hangers and Supports for Electrical Systems>>​.

CNI CABLE INSTALLATION

Install LANL-supplied CNI cables according to LANL ESM Chapter 19 - Communications, Section D60, Communications; <<NFPA 70>>​ (including Article 800); and requirements in this Section.

Handle and install cable according to cable manufacturers’ instructions. Manufacturer’s installation instructions must be available at the work site.

Completely and thoroughly swab raceways before installing cable.

Clean foreign matter from interior of boxes before installing cables.

Store cable for 24 hours in the installation area ambient temperature before installing.

Do not “through-pull” cables at boxes, fittings, or cabinets where a change of raceway alignment occurs.

Install LANL-furnished fiber-optic cable(s) from each CNI outlet to the CNI patch panel racks in the secure telecommunications (server) room. Leave 15 feet of slack at the patch panel end and 18 inches of slack at the outlet end.

Fiber optic cables may not be terminated until lock cores are installed in CNI outlet boxes.

CNI OUTLET INSTALLATION

Surface mount LANL-supplied CNI outlets with centers at the following heights:

CNI outlets: Center 44 inches above the finished floor.

CNI outlets at lab benches and counters: Center 44 inches maximum above the finished floor. Coordinate locations to be above or completely within, bench and counter backsplashes.

Verify location of each CNI outlet by field measurements and coordination with other trades.

Install each outlet at a location suitable to serve its intended purpose.

Install CNI outlets so they will have 6 inches of separation from all other outlets.

      - ***************************************************************************************

      - Retain the following Article when conduit, wireway and/or CNI cable are in project-scope. Retain the applicable paragraphs based on project-scope.

      - ***************************************************************************************

IDENTIFICATION

Band CNI raceways, wireways and conduit with 3/4-inch wide, red plastic tape on 5-foot centers, beginning with the first band within 2 inches of the POB, on both sides of wall, ceiling, and floor penetrations, at every change of direction and within 2 inches of wireway penetration. Apply tape after painting is completed.

Positively identify and label each cable using an approved light source and at both ends using a numbering scheme that complies with Section << 27 1000 - Structured Cabling>> and instructions from the LANL Telecommunications Group.

ACCEPTANCE TESTING

Perform testing with a Fluke Model OTDR (Optical Time Domain Reflectometer). Subcontractor must allow the LANL Telecommunications Group to download and then erase LinkWare test results from the test equipment. Under no circumstances may Subcontractor save secure test results to a database other than a LANL-owned database, nor remove test results from LANL site.

Submit test reports in a Fluke Linkware format for each installed and terminated fiber and Category 5E or 6A horizontal cable. Physically deliver test results to the LANL Telecommunications Group to download into their database.

LANL Telecommunications Group will review the electronic test results on all Category 5E or 6A UTP (unshielded twisted pair) and fiber cables for conformance. Cables must meet all testing requirements before cable is accepted.

FIELD QUALITY CONTROL

CNI raceway system will receive a comprehensive visual inspection by LANL Telecommunications Group Site Coordinator and LANL Telecommunications Group Inspector before being covered.

Correct deficiencies identified by this inspection and arrange for re-inspection.

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 27 1500.18, REV. 4, DATED APRIL 15, 2026.