Section 28 0528 
Pathways for Electronic Security

  - ************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 5 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., SECTION INCLUDES in PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Electrical/Security POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable sections from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality sections.

  - ************************************************************************************************************

PART 1 - GENERAL

Section Includes

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements.

      - ***************************************************************************************

Electronic Physical Security System (PSS) rough-in that originates in Argus Field panels (AFPs) located in the entrance telecommunications room and extends to LANL-furnished Automated Access Control System (AACS) and Interior Intrusion Detection System (IIDS) components indicated on the Drawings.

      - ***************************************************************************************

      - Retain the following paragraph to match project requirements.

      - ***************************************************************************************

Automated Access Control System (AACS) includes:

Door access control systems with Remote Access Panels (RAPs), biometric units, and door hardware (strikes and latches) with key overrides.

Turnstile access control systems with RAPs. Turnstile egress may be accomplished with pushbutton or RAP.

      - ***************************************************************************************

      - Retain the following paragraph to match project requirements.

      - ***************************************************************************************

Interior Intrusion Detection System (IIDS) includes:

Volumetric, perimeter, and/or point contact detectors.

Door sensor switches.

RELATED REQUIREMENTS

Section << 01 2500 - Substitution Procedures>>

Section << 01 3300 - Submittal Procedures>>

Section << 08 7100 - Door Hardware>>

Section << 26 0526 - Grounding and Bonding for Electrical Systems>>

Section << 26 0533 - Raceways and Boxes for Electrical Systems>>

Section << 33 7119 - Electrical Underground Ducts and Manholes>>

REFERENCE STANDARDS

NECA 1 - Standard for Good Workmanship in Electrical Construction.

NEMA 12 - Electrical Enclosure.

NFPA 70 - National Electrical Code.

COORDINATION

Coordinate installation of PSS rough-in (pathways and cables) with the LANL Security Systems Group.

Coordinate the layout of PSS equipment in the telecommunications rooms with both the LANL Telecommunications Group and the LANL Security Systems Group. Verify that adequate space exists for equipment.

Coordinate electrical requirements for electric strikes/latches with the LANL Security Systems Group. Refer to Electric Door Hardware heading below.

Coordinate required quantities of PSS cables and delivery schedule with the LANL Security Systems Group.

LANL PERFORMED WORK

LANL will make final wiring connections to PSS field devices and control equipment after beneficial occupancy.

INFORMATIONAL SUBMITTALS AT CLOSEOUT

Submit the following in accordance with Section ​<< 01 3300 - Submittal Procedures>>​:

Test Reports: Provide inspection and test report for each PSS power, signaling, and control cable.

Record Drawings: Provide record drawings showing as-installed PSS raceways, boxes, and cables.

Quality Assurance

Conform to requirements of <<NFPA 70>> (NEC).

Furnish products listed and labeled by a Nationally Recognized Testing Laboratory (NRTL)

DELIVERY, STORAGE, AND HANDLING

Receive, store, protect, and handle products and materials according to <<NECA 1>>.

PART 2 - PRODUCTS

LANL-Furnished Materials for SUBContractor INstallation (GFE)

Argus Field Panel (AFP) Assembly enclosures

Specialty PSS boxes.

Fiber and Copper for data and control of PSS field devices. Subcontractor to provide required cable lengths.

LANL Furnished and Installed Equipment

LANL will furnish and install the PSS field devices (AFP internal components, batteries, RAPS, biometric units, volumetric sensors, door sensor switches, power supplies, and control equipment).

      - ***************************************************************************************

      - Retain the following article if substitutions are allowed on the project

      - ***************************************************************************************

PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section << 01 2500 - Substitution Procedures>>.

Raceways and Boxes

      - ***************************************************************************************

      - Retain one (or more) of the following three paragraphs to indicate which type of raceway to use on the project. Check with LANL to ascertain which is acceptable for the project. EMT has not always been allowed.

      - ***************************************************************************************

Use electrical Metallic tubing (EMT) and fittings for all interior PSS raceways unless indicated otherwise.

Use intermediate metal conduit (IMC) and fittings for all interior PSS raceways unless indicated otherwise.

Use rigid galvanized steel (RGS) and fittings for all exterior PSS raceways unless indicated otherwise.

Provide 4-11/16 square, 2-1/8 inch deep outlet boxes for PSS field devices (e.g. RAPs, biometric units, security terminal boxes, and volumetric detector units). Provide plaster rings (mud rings) for flush mount boxes that match the thickness of the wallboard and the mounting requirements of the PSS field device. Provide support to prevent movement of the box.

LANL will furnish as government-furnished equipment (GFE) the following specialty boxes and enclosures for installation by the Subcontractor:

10 inch x 10 inch x 4 inch hinged cover, surface-mounting junction boxes.

6 inch x 6 inch x 4 inch hinged cover, surface-mounting junction boxes.

16 inch x 20 inch x 8 inch AFP enclosure(s), 24 inch x 20 inch x 8 inch FTB enclosure(s) and 20 inch x 20 inch x 8 i Battery enclosure for wall-mounting.

4 inch x 4 inch x 4 inch hinged cover, surface-mounting junction boxes.

Mounting brackets for RAPs and biometric units.

6 inch x 6 inch x 36 inch wireways (gutters) with all closure plates, gaskets and fittings.

16 inch x 20 inch x 10 inch hinged cover, surface-mounting junction boxes.

16 inch x 12 inch x 8 inch hinged cover, surface-mounting junction boxes.

Refer to Section << 26 0533 - Raceways and Boxes for Electrical Systems>>​ for additional material requirements.

      - ***************************************************************************************

      - The following article is automatically activated when door access (AACS) is activated in PART 1.

      - ***************************************************************************************

Electric Door Hardware

Furnish electric door hardware (strikes, panic bars, fire exit hardware, latches) with key override for each access-controlled door or set of doors as indicated on the Drawings.

Provide 24-volt dc door strikes, panic bars, and fire exit hardware that operate on 0.5 (1/2) amperes or less, are easily serviceable, are electrically compatible with the LANL-furnished PSS, and are functionally compatible with each access-controlled door and with finish compatible with the other door hardware.

Refer to project door and hardware schedule for proper installation of door strikes/latches and raceway routing.

Do not make penetrations through, or mount raceways/cables to, fire door frames.

Refer to Section << 08 7100 - Door Hardware>> for material requirements.

PSS Cables

LANL will furnish the PSS cables as GFE for installation by the Subcontractor. The following information is provided for determining conduit sizes and estimating installation labor:

3 pair 22 AWG with overall shield, NEC Type CMG, 0.27-inch nominal O.D.

2/C 18 AWG stranded cable, NEC Type CMG, 0.2-inch nominal O.D.

Coordinate cable lengths and delivery schedule with the LANL Security Systems Group.

PART 3 - EXECUTION

    - **********************************************************************************************

      - Retain the following article when existing construction is affected.

    - **********************************************************************************************

EXISTING WORK

After security system equipment has been removed by LANL Security Systems Group:

Remove abandoned PSS cables.

Remove abandoned raceways and boxes.

Install blank cover for abandoned boxes not removed.

Maintain access to existing PSS connections remaining active and requiring access. Modify installation or provide access panels.

EXAMINATION

Verify interior of the building has been protected from weather.

Verify that installation of telecommunications rooms is complete.

Examine raceways and building finishes for compliance with installation tolerances and other conditions affecting performance of the PSS.  Do not proceed with installation until unsatisfactory conditions have been corrected.

Raceway and Box Installation - General

Install a complete raceway and box system for the PSS.

Select raceway sizes based on the following factors:

Minimum raceway size: 1-inch unless indicated otherwise.

Install PSS raceways and boxes as follows:

Not more than 100 ft. of raceway between pull points.

No more than 180 degrees of raceway bends between pull points.

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements. Typical raceway benders have a bending radius of from 4.5 times internal diameter to 6 times internal diameter. Factory elbows will follow these ratios unless special elbows are purchased. Sometimes, larger raceways are used because cables with ends are used and the larger bending radius is specified to allow the cable ends/plugs to fit in the raceway. If this is the case, retain the following paragraph. If no pre-terminated cables are being used, the following can be omitted.

      - ***************************************************************************************

Make PSS raceway bends as follows:

For raceways 2-inches and smaller, make inside radius of bends not less than 6 times the internal diameter of the raceway, or use factory-made raceway elbows

For raceways larger than 2-inches, make inside radius of bends not less than << 10; or  6>> times the internal diameter of the conduit.

Install raceways concealed in walls and above ceilings to the extent practicable.

Refer to Section << 26 0533 - Raceways and Boxes for Electrical Systems>>​ for additional installation requirements.

PSS Service Installation

Install PSS service raceways; refer to Section << 33 7119 - Electrical Underground Ducts and Manholes>>.

AFP, FTB, Battery, AND OTHER Enclosure Installation

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements. Boxes required per location is specific to project requirements and will be sown on the drawings.

      - ***************************************************************************************

Install AFP, FTB, wireway, battery, and fiber optic enclosures in the entrance telecommunications room and/or other locations indicated on the Drawings. Contact LANL Security Systems Group for a set of current standard security system infrastructure drawings

Install 6 inch x 6 inch x 36 inch feed-through  <<NEMA 12>> upper wireway with top approximately 9 feet above finished floor. Mount with hinged edge down.

Locate AFP enclosure with top approximately 7 feet above finished floor and centered on upper wireway.

Install 16 inch x 12 inch x 8 inch fiber optic cabinet enclosure below the upper wireway and centered on the AFP enclosure. Connect fiber optic cabinet to upper gutter box with one 2 inch raceway.

Locate FTB enclosure with top approximately 4 ft -10 inches above finished floor and aligned with the AFP enclosure above. Connect FTB to AFP with two 3 inch raceways.

Install 6 inch x 6 inch x 36 inch feed-through <<NEMA 12>> lower wireway with bottom approximately 2 feet above finished floor below and centered on the FTB enclosure. Mount with hinged edge up. Connect lower wireway to FTB with two 3 inch conduits. Connect lower wireway to upper wireway with two 3 inch raceways (one on each side of wireways above).

Locate battery enclosure with top approximately 22 inches above finished floor and centered on the lower wireway. Connect battery enclosure to lower wireway with one 3/4 inch raceway.

Coordinate final AFP, FTB, wireway, battery and fiber optic enclosure quantities and locations in the telecommunications room with the LANL Telecommunications Group and the LANL Security Systems Group.

Provide a dedicated space that is 7-ft wide, 9-ft high, and 14-inches deep for each AFP, FTB, and BAT installation.  Provide 36 inches of clear space in front of these boxes.

Provide a 20-ampere, 120-volt, individual branch circuit to each BAT enclosure.

Connect with 3/4 inch raceway to receptacle outlet provided with each battery enclosure.

Install a 1-inch raceway from the wireway to a point above the telephone terminal blocks or fiber termination board. Coordinate location with the LANL Telecommunications Group and LANL Security Systems Group.

AACS/iidsJunction Box Installation

Install one 16 inch X 12 inch X 8 inch junction box at each location indicated on drawings. Contact LANL Security Systems Group for a set of current standard security system infrastructure drawings.

Connect 16 inch X 12 inch X 8 inch junction box to upper wireway of AFP complex with one 2 inch raceway.

Make raceway connections to top, bottom, and/or sides, but not to the back of AACS/IIDS junction boxes.

      - ***************************************************************************************

      - The following article is automatically activated when door access (AACS) is activated in PART 1.

      - ***************************************************************************************

dOOR junction box installation

Install one 10 inch X 10 inch X 4 inch junction box and one 6 inch X 6 inch X 4 inch junction box above door frame and below the suspended ceiling on the high security side of each controlled door. Contact LANL Security Systems Group for a set of current standard security system infrastructure drawings.

For single doors mount 10 inch X 10 inch x 4 inch junction box with bottom 8 inches above door frame and centered on door. Mount 6 inch X 6 inch X 4 inch junction box with bottom 1 inch above door frame and align edge of box with the non hinge side edge of the door frame.

For double doors mount 10 inch X 10 inch x 4 inch junction box with bottom 12 inches above door frame and centered between doors. Mount 6 inch X 6 inch X 4 inch junction box with bottom 1 inch above door frame and centered on 10 inch X 10 inch X 4 inch junction box.

Connect 10 inch X 10 inch X 4 inch junction box to the nearest junction box with one 1 inch raceway as indicated on the drawings.

Connect 6 inch X 6 inch X 4 inch junction box to 10 inch X 10 inch X 4 inch junction box with one 1 inch raceway.

Make raceway connections to the top, bottom, and/or sides, but not to the back of AACS junction boxes.

Make raceway connections a minimum of 1 i from back of box.

      - ***************************************************************************************

      - The following article is automatically activated when door access (AACS) is activated in PART 1.

      - ***************************************************************************************

RAP and Biometric Unit Outlet Installation

      - ***************************************************************************************

      - Edit the following paragraphs to match project requirements. Boxes required per location is specific to project requirements. Mounting requirements may also be specific to project requirements.

      - ***************************************************************************************

At interior access-controlled doors, install one/ two flush mounted 4-11/16 square, 2-1/8 inch deep outlet boxes on the low security side and one flush mounted 4-11/16 square, 2-1/8 inch deep outlet box on the high security side as indicated on the drawings. Contact LANL Security Systems Group for a set of current standard security system infrastructure drawings and alternate mounting methods.

For a single door, locate outlet boxes on the strike side of the door with centers 39 inches above the finished floor.  Ensure box is located so that person accessing area is out of the swing of the door.

For a double door, locate the outlet boxes on the active leaf side of the door with centers 39 inches above the finished floor.  Ensure box is located so that person accessing area is out of the swing of the door.

Provide each box with a two-gang plaster ring that matches the thickness of the wallboard.

Provide supports securely attached to the wall studs to prevent movement of the boxes.

At each location provide a minimum 24-inch x 24-inch clear and flat surface centered on the outlet boxes suitable for mounting RAP and HGU brackets.

Connect boxes with 1 inch raceways as indicated on the drawings.

Connect RAP outlet box to the nearest junction box with one 1 inch raceway as indicated on the drawings.

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements. Boxes required per location is specific to project requirements.

      - ***************************************************************************************

On the low security side of exterior access-controlled doors install one surface-mounted 16 inch X 20 inch X 10 inch box and one exterior HGU mounting bracket with bottom of box and bracket approximately 39 inches above finished floor. Install one surface-mounted 12 inch X 16 inch X 8 inch box directly under and center on HGU mounting bracket.

If the high side of the door is also on the exterior, install one 16 inch X 20 inch X 10 inch box with bottom of box approximately 39 inches above finished floor as indicated on the drawings If the high side of the door is on the interior, install one flush mounted 4-11/16 square, 2-1/8 inch deep outlet box.

Connect the interior box to the nearest junction box with one 1 inch raceway as indicated on the drawings.

Install a 3/4 inch raceway connecting the interior junction box and the 16 inch X 20 inch X 10 inch box.

Install a 3/4 inch raceway connecting the 16 inch X 20 inch X 10 inch box and the exterior HGU mounting bracket.

Install a 3/4 inch raceway connecting the 12 inch X 16 inch X 8 inch box and the exterior HGU mounting bracket.

Install one duplex 15-ampere, 125-volt receptacle, fed from an individual branch circuit, in each 12 inch X 16 inch X 8 inch box. Install a 3/4 inch raceway from the 12 inch X 16 inch X 8 inch box to local electrical panel.

      - ***************************************************************************************

      - The following article is automatically activated when door access (AACS) is activated in PART 1.

      - ***************************************************************************************

Electric Hardware installation

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements. Boxes required per location is specific to project requirements.

      - ***************************************************************************************

Install electric door hardware at each access-controlled door as indicated on the Drawings and in accordance with the installation requirements Section << 08 7100 - Door Hardware>>. Refer to project door and door hardware schedule for proper installation of door strikes/latches and raceway routing. Contact LANL Security Systems Group for a set of current standard security system infrastructure drawings.

Install a 1/2 inch raceway from the door strike/latch to the 6 inch X 6 inch X 4 inch junction box / 10 inch X 10 inch X 4 inch junction box as indicated on the drawings. Do not penetrate through, or attach raceway to, any security door frame that is a fire door.

Coordinate rough-in with the requirements of the specific hardware installed on each door. Typical rough-in locations are as follows:

Door strike integral to door frame: rough-in raceway to strike side of door frame.

Panic bar or latch on door leaf: rough-in raceway to hinge side of door frame.

volumetric detector outlet installation

      - ***************************************************************************************

      - Edit the following paragraph to match project requirements. Boxes required per location is specific to project requirements.

      - ***************************************************************************************

Coordinate the quantity and locations of volumetric detectors with the LANL Security Systems Group.

For estimating purposes use a quantity of not less than one detector per 100 sq. ft. of protected area.

Furnishings, ceiling height, room geometry, and equipment in the protected space may necessitate a greater density of detectors.

Install flush/surface mounted 4-11/16 square, 2-1/8 inch deep outlet boxes for volumetric detectors as indicated on the Drawings or as required by the Security Systems Group. Contact LANL Security Systems Group for a set of current standard security system infrastructure drawings.

For spaces with ceilings not more than 9 ft above finished floor, locate the outlet boxes with centers 8 ft above the finished floor.

For spaces with ceilings more than 9 ft above finished floor, install two outlet boxes at each location.

Center the lower outlet box 8 ft above the finished floor and the upper outlet box 8-inches above the lower outlet box or as required by the Security Systems Group.

Install a 1 inch raceway connecting the two boxes.

Provide each flush mounted box with a double-gang plaster ring that matches the thickness of the wallboard.

Install a dedicated 1-inch raceway loop to serve no more than 5 outlet boxes.

PSS Cable Installation

Install GFE PSS cables after painting and similar activities that could damage cables have been completed.

Clean foreign matter from interior of boxes and raceways before installing PSS cables.

Pull all cables to the FTP enclosure(s) Leave 10 ft of slack in each cable at the FTP enclosure(s).

Leave 3 ft of slack in each cable at the PSS field device outlet boxes.

Pull no more than 15 Belden 8303 cables through a 2 inch raceway.

Pull no more than 5 Belden 8303 cables through a 1 inch raceway.

Install cables in accordance with the following schedules. Provide a slack loop of the cable around the inside perimeter of each junction box. All cables are continuous with no splices.

| Cable Routing Requirements - General |  |  |
| --- | --- | --- |
| From | To | Cable Type (GFE) |
| FTB Enclosure | Biometric unit outlet box | One Belden 8303 |
| FTB Enclosure | Each RAP outlet box | Two Belden 8303 |
| FTB Enclosure | Each 6” X 6” X 4” junction box | Single leaf door: One Belden 8303 Double leaf door: Two Belden 8303 |
| FTB Enclosure | Each volumetric detector outlet box | One Belden 8303 |
| FTB Enclosure | Door Strike/Latch | One 2/C 18AWG cable |

Hidden Paragraph

| Cable Routing Requirements – Turnstiles |  |  |
| --- | --- | --- |
| From | To | Cable Type (GFE) |
| FTB Enclosure | Each RAP | Two Belden 8303 |
| FTB Enclosure | Each pushbutton outlet box | One Belden 8303 |
| FTB Enclosure | Each turnstile channel top channel | One Belden 8303 |
| Turnstile Top Channel | Each pushbutton outlet box | One 2/C 18AWG cable |

Uniquely identify each cable at both ends using a numbering scheme that complies with instructions from the LANL Security Systems Group; use a tag or an indelible marker.

The LANL Security Systems Group will install PSS equipment and field devices and will terminate all PSS cables.

GROUNDING

Ground PSS raceways and boxes following Section << 26 0526 - Grounding and Bonding for Electrical Systems>>  using the raceway system as the equipment grounding conductor.

FIELD QUALITY CONTROL

Test power, PSS cables for continuity, shorts, and unintentional grounds.

Verify proper labeling of cables.

Submit test and inspection report.

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 28 0528, REV. 5, DATED APRIL 15, 2026.