Section 28 4600 
Fire Detection and Alarm

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 6 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Fire POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable sections from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality sections.

      - Seismic:  To edit this section for job-specific seismic requirements, refer to author notes that indicate “Seismic,” and the document, Seismic Spec-Editing for Electrical/Fire Alarm Components (“Guide,” posted under References on the LANL Master Specifications page) for guidance on properly editing this section.

      - NOTE: Scope of work in this section should match the scope of work in the drawing package including codes and standards references.

  - *************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

      - ***************************************************************************************

      - The following three paragraphs are designer choices. The choice field in the second paragraph activates relevant content in Article INSTALLATION.

      - ***************************************************************************************

Circuits from protected premises to supervising station, including raceways.

<< Replacement and removal; or  Modification>> of existing fire alarm system components, wiring, and raceways indicated.

Maintenance of fire alarm system under subcontract for specified warranty period.

Provide an addressable fire alarm system consisting of, but not limited to, the following components:

        - ******************************************************************************

        - Edit subparagraphs below to match project fire alarm system requirements. Supplement list for devices or equipment not listed. Specific details of the required system can be provided as necessary. Modify description for modifications of existing systems.

        - ******************************************************************************

Fire Alarm Control Units (FACU) Components

Raceways

Junction Boxes and Backboxes

Wiring

Test Equipment

Surge Protection Devices (SPD)

Manual Transfer Switch

Panel Receptacles

      - ***************************************************************************************

      - The following Sections are not referenced outside the RELATED REQUIREMENTS Article. The designer must select them as applicable.

      - Sections << 01 4216 - Definitions>>, << 01 4000 - Quality Requirements - Non-Nuclear>>, << 01 6000 - Product Requirements>>, << 01 7839 - Project Record Documents>>, << 02 4115 - Electrical Demolition>>, << 07 8400 - Firestopping>>, << 08 3323 - Overhead Coiling Doors>>, << 21 1200 - Fire-Suppression Standpipes>>, << 21 2200 - Clean-Agent Fire-Extinguishing Systems>>, << 21 3000 - Fire Pumps>>, << 22 0535 - Electric Heat Tracing Systems>>, << 23 3300 - Air Duct Accessories>>, << 26 2933 - Controllers for Fire Pump Drivers>>, << 27 1000 - Structured Cabling>>, and << 27 3000 - Voice Communications>>.

      - ***************************************************************************************

RELATED REQUIREMENTS

Section << 01 2500 - Substitution Procedures>>

Section << 01 3300 - Submittal Procedures>>

Section ​​<< 01 4000 - Quality Requirements - Non-Nuclear>>​​​

Section ​​<< 01 4216 - Definitions>>​​

Section ​​<< 01 6000 - Product Requirements>>​​

Section ​<< 01 7700 - Closeout Procedures>>​

Section << 01 7823 - Operation and Maintenance Data>>

Section ​<< 01 7839 - Project Record Documents>>​

Section ​<< 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>​

Section ​<< 02 4115 - Electrical Demolition>>​

Section << 07 8400 - Firestopping>>

Section << 08 3323 - Overhead Coiling Doors>>

Section ​<< 08 7100 - Door Hardware>>​

Section ​<< 09 9100 - Painting>>​

Section ​​<< 21 1200 - Fire-Suppression Standpipes>>​​

Section << 21 1300 - Fire-Suppression Sprinkler Systems>>

Section << 21 2200 - Clean-Agent Fire-Extinguishing Systems>>

Section << 21 3000 - Fire Pumps>>

Section << 22 0535 - Electric Heat Tracing Systems>>

Section << 23 3300 - Air Duct Accessories>>

Section << 26 0529 - Hangers and Supports for Electrical Systems>>

Section << 26 0533 - Raceways and Boxes for Electrical Systems>>

Section << 26 0548.16 - Seismic Controls for Electrical Systems>>

Section << 26 0553 - Identification for Electrical Systems>>

Section << 26 2933 - Controllers for Fire Pump Drivers>>

Section << 26 2726 - Wiring Devices>>

Section << 27 1000 - Structured Cabling>>

Section << 27 3000 - Voice Communications>>

REFERENCE STANDARDS

ABA Standards - ABA Accessibility Standards.

ADA Standards - 2010 ADA Standards for Accessible Design.

ASCE 7 - Minimum Design Loads and Associated Criteria for Buildings and Other Structures.

ASME A17.1 - Safety Code for Elevators and Escalators Includes Requirements for Elevators, Escalators, Dumbwaiters, Moving Walks, Material Lifts, and Dumbwaiters with Automatic Transfer Devices.

DOE-STD-1066 - Fire Protection.

ICC (IBC) - International Building Code.

ICC (IEBC) - International Existing Building Code.

ICC (IFC) - International Fire Code.

NECA 305 - Standard for Fire Alarm System Job Practices.

NFPA 70 - National Electrical Code.

NFPA 72 - National Fire Alarm and Signaling Code.

NFPA 76 - Standard for the Fire Protection of Telecommunications Facilities.

NFPA 90A - Standard for the Installation of Air-Conditioning and Ventilating Systems.

NFPA 101 - Life Safety Code.

UL 268 - Standard for Smoke Detectors for Fire Alarm Systems.

UL 464 - Standard for Audible Signaling Devices for Fire Alarm and Signaling Systems, Including Accessories.

UL 497B - Standard for Protectors for Data Communications and Fire-Alarm Circuits.

UL 1424 - Cables for Power-Limited Fire-Alarm Circuits.

UL 1449 - Standard for Surge Protective Devices.

UL 1480 - Standard for Speakers for Fire Alarm and Signaling Systems, Including Accessories.

UL 1484 - Residential Gas Detectors.

UL 1971 - Standard for Signaling Devices for the Hearing Impaired.

UL 2034 - Standard for Single and Multiple Station Carbon Monoxide Alarms.

UL 2075 - Standard for Gas and Vapor Detectors and Sensors.

DEFINITIONS

For definitions and acronyms, refer to COE Glossary of Terms. definitions exist for the following terms: AHJ, FDAR, LBO, STR, Subcontractor among others.

AFF – Above finished floor

AHJ – Authority having Jurisdiction

DACT – Digital Alarm Communicator Transmitter

DTMF – Dual-Tone, Multi-Frequency

DSS – Designated Seismic Systems

ECF – Emergency Two-Way Communication Systems

EMT – Electrical Metallic Tubing

EOC – Emergency Operations Console

EWFD – Early Warning Fire Detection

FACU – Fire Alarm Control Units

FOD – Facility Operations Director/Facility Operations Directorate

FDAR – Facility Design Authority Representative

FMC – Flexible Metal Conduit

FPO – Fire Protection Office

IDC – Initiating Device Circuits

IFC – Issue for Construction

IMC – Intermediate Metal Conduit

LBO – LANL Building Official

MTS – Manual Transfer Switch

NAC – Notification Appliance Circuits

NAPP – Notification Appliance Power Panels

PE – Project Engineer

PVC – Polyvinyl Chloride

RMC – Rigid Metal Conduit

RTRC – Reinforced Thermosetting Resin Conduit

SFD – Standard Fire Detection

SLC – Signaling Line Circuits

SPD – Surge Protection Devices

STR – Subcontract Technical Representative

UPS – Uninterruptible Power Supply

UV/IR – Ultraviolet/Infrared

VEWFD – Very Early Warning Fire Detection

DESIGN

      - ***************************************************************************************

      - Edit system design description to match the project fire alarm system requirements. Include details to supplement the shop drawings, as required. The example list should not be considered comprehensive for any specific project. Projects in high explosives areas or per NEC Article 500 hazardous locations will require additional specialized equipment and system characteristics not included in this section.

      - ***************************************************************************************

System Design:

Pathways: Survivability Level << 1;  2; or  3>>.

System circuits configured as follows:

          - **********************************************************************

          - The following subparagraphs are designer choices.

          - **********************************************************************

Signaling Line Circuits or Network Circuits between FACUs/Transponders Class X

Signaling Line Circuits (SLC) Class B

Initiating Device Circuits (IDC) Class B

Notification Appliance Circuits (NAC) Class B

Emergency Two-Way Communication Class B

Emergency Control Function Circuits Class D.

        - ******************************************************************************

        - The following subparagraphs are designer choices.

        - ******************************************************************************

SLC zones configured as Separate Circuits or a Hybrid Class A Isolator Loops with Class B Branches.

SLCs shall not exceed 80 percent total device capacity.

Calculations: Use the UL max current draw for notification appliances.

NACs: Provide end-of-line voltages 10% greater than the minimum device operating voltage, starting with the panel cut-off voltage at the terminals. Current draw not exceeding 80% of maximum capacity with the starting voltage at 20.4 VDC.

Batteries: Sized for 24 hours of standby and 10 minutes (minimum) of alarm, and 15 minutes (minimum) for Voice Evacuation Systems, fully loaded SLCs, and 10 percent of indicator lights and other auxiliary features active. De-rating factor: 50 percent.

The FACU LED Annunciator/Switch Card pre-defined disable groups shall correspond to an individual Control Relay for disabling emergency control functions independently, and a separate group for all notification appliances (except for any sprinkler system waterflow audible alarms).

Provide dedicated Surge Protection Devices (SPD) on the Primary Power Circuit, and all Fire Alarm and Control Circuits (IDC, NAC, SLC, etc.) that extend beyond or enter a building.

Provide a Remote LED Alarm Indicator for: Duct Smoke Detectors located outside, above a ceiling, or 10 feet AFF, when the Duct Smoke Detector is in a separate space other than the associated Control Relay.

ACTION SUBMITTALS

Provide the following submittals per Section << 01 3300 - Submittal Procedures>>.

Certifications

Within 30 days after Notice to Proceed, qualifications of the fire alarm installing firm.

Within 30 days after Notice to Proceed, qualifications of the fire alarm system technician.

Designated Seismic System: Special Certification from Manufacturer per <<ASCE 7>>, Section 13.2.2

FACU Program: Provide Programming file for Fire Alarm System minimum 10 working days prior to Pre-Final Test. Note: FPO will provide a copy of the programming file for Fire Alarm Modification Projects, upon request during Title III.

Test Plan: Submit test plan for the final acceptance tests, 10 working days prior to Pre-Final Test.

DELEGATED DESIGN SUBMITTALS

Provide the following submittals per Section << 01 3300 - Submittal Procedures>>.

Submit delegated design submittals for review at least 30 days prior to scheduled start of fire alarm system installation. Installation shall not proceed without 100 percent IFC Shop Drawing approval by LANL (Fire Protection Office, and the FDAR or LBO, appropriately for the work type).

Mark the first package as a 60 percent Shop Drawing Design, followed by 90 percent, then 100 percent. A design without comments may proceed to the 100 percent design with the concurrence of the LANL Fire Protection Office. Address comments with additional design review percent.

Draft submittals (i.e., 60 percent, 90 percent & 100 percent) shall be marked with the appropriate alphabet, starting with A for the initial. Final IFC package shall be marked with a numerical revision, starting with 0. Subsequent revisions shall be marked with the next sequential revision number.

Shop drawings shall follow the LANL CAD Standards Manual.

Catalog Data for all equipment and devices including Installation Instructions.

Design Package: Submit all information required for plan review and permitting by FPO/AHJ, including but not limited to floor plans, riser diagrams, and description of operation:

Copy (if any) of the List of Data required by FPO/AHJ.

Clear and concise description of operation, with input/output matrix similar to that shown in <<NFPA 72>> Appendix A.14.6.2.4, and complete listing of software required.

System zone boundaries and interfaces to fire safety systems as indicated in <<NFPA 72>>.

Location of all components, circuits, and raceways; mark components with identifiers used in control unit programming.

Circuit layouts; number, size, and type of raceways and conductors

Provide calculations as a sheet in the design package drawings which includes

System Battery Load

Voltage Drop calculations for notification appliances

Provide settings for each fire alarm device on the plans and risers including addresses:

Candela

Loudness

Wattage

Voltage – 25 VRMS or 70 VRMS

Provide location of and conductor pathway to electrical panels, telecommunication boards, and other equipment supplying primary or secondary power.

Provide location and type of all interfaced systems for monitoring or emergency control functions.

Provide installation specific wiring and termination details for monitoring module and control relays/modules at the monitored or controlled equipment.

Provide elevation drawings.

Provide a sheet with the Materials and Parts List.

List of all devices on each signaling line circuit with a Points/Address List with Descriptions on the Riser Diagram.

Manufacturer's detailed data sheet for each component, including wiring diagrams, installation instructions, and circuit length limitations, if applicable.

Air-Sampling Smoke Detection Systems (VESDA): Include air-sampling pipe network layout with sampling ports identified; include calculations demonstrating compliance with specified requirements.

Description of power supplies; if secondary power is by battery include calculations demonstrating adequate battery power.

Detailed drawing of graphic annunciator(s).

        - ******************************************************************************

        - Seismic: See Seismic Specification Editing Guide discussed in first author’s note for editing guidance.

        - ******************************************************************************

Required seismic design documentation:

Include dimensioned representations or plans and elevations that identify the weight and the location of the center of gravity.

Indicate field anchorage or mounting provisions to hold the component in place and resist forces derived from the criteria specified in Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC);  26 0548.16 - Seismic Controls for Electrical Systems; or  _______>>.

Identify anchors and other mounting devices.

Include information on the size, type, and spacing of factory-installed mounting brackets, holes, and other mounting provisions.

Supporting calculations for seismic design.

INFORMATIONAL SUBMITTALS

Provide the following submittals per Section << 01 3300 - Submittal Procedures>>.

      - ***************************************************************************************

      - Operations and Maintenance Manual Submittals are based on new projects or major modifications to the Fire Alarm System.

      - ***************************************************************************************

Operation & Maintenance Manual

Follow the requirements of Section ​<< 01 7823 - Operation and Maintenance Data>>​.

Submit project-specific operating and maintenance instruction manuals upon successful completion of the Final Acceptance Test.

Provide in an electronic format shall consist of all items combined into one PDF file.

Submit operating and instruction manuals that include the as-built calculations and drawings.

Provide complete, step-by-step recommended and required testing instructions with frequency, methods, and troubleshooting information for all devices and equipment.

Maintenance instructions shall provide the following information:

Instructions for replacing any components of the system, including internal parts.

A list of recommended spare parts.

Instructions and schedule for periodic cleaning and adjustment of equipment meeting <<NFPA 72>>.

A list of all equipment with the address and telephone number of the manufacturer and local supplier.

Test Reports

        - ******************************************************************************

        - An installer’s preliminary test report is required when additional assurance is needed that the system is ready for LANL pre-final and final testing with the fire alarm system reporting to the LANL supervising station at the Emergency Operations Console (EOC). This is not intended to require a report for LANL pre-testing of the fire alarm system and it’s reporting to the EOC, which precedes the final acceptance test. A statement of compliance can also be required. Neither are appropriate for system modifications, which often require final acceptance test immediately after tie-in to the existing system. Test plans and final test reports are required by the IBC/IFC and NFPA 72 for all work.

        - ******************************************************************************

Installer’s Preliminary Test Report: Submit report of the installing subcontractor’s preliminary tests in accordance with <<NFPA 72>> and indicating system status and corrective actions required ten working days before Pre-Final Test.

Statement of Compliance per <<ICC (IFC)>>  Section 901.2.1 and <<NFPA 72>> Section 7.5.2.

Final Test Report: After final acceptance test, submit test reports.

Provide Project Record Documents upon completing Final Acceptance Test

FACU Program file

Provide the electronic As-Built drawing files in “.pdf”

Provide Record of Completion and associated documentation for the completed system according to <<NFPA 72>>.

Final CAD As-Built Drawing Package

Submit all CAD files (including .dwg, .xref, etc.) in a .zip folder to project-dcrm@lanl.gov upon completing Final Acceptance Test.

      - ***************************************************************************************

      - The following paragraph is a designer choice based on project-specific requirements.

      - ***************************************************************************************

Warranty

See Section << 01 7700 - Closeout Procedures>>, for additional warranty requirements.

Warrant all equipment and wiring for mechanical and electrical defects for not less than one year (365 days) from the date of final acceptance test.

QUALITY ASSURANCE

Qualifications of Subcontractor producing Shop Drawings:

Be qualified to design Fire Alarm Systems based on the following:

Have successfully designed at least 20 Fire Alarm Systems of equivalent nature and scope to the system described in this section.

Utilize a qualified Fire Alarm System Technician who is NICET III or IV Certified, or a Registered Fire Protection Engineer in the state of NM, employed by the installer.

Be a Manufacturer Factory-Certified Representative for the specified Fire Alarm System.

Qualifications of Subcontractor installing the Fire Alarm System:

Have successfully installed and field-tested at least 20 Fire Alarm Systems of equivalent nature and scope to the system described in this section and providing maintenance service as a regular part of their business.

Installer/Programmer Personnel: Provide services of a Journeyman Electrician for raceways or a Low-Voltage Electrician for wiring, and a minimum of five years of experience installing Fire Alarm Systems.

Be factory trained in the theory, operation, installation, and troubleshooting of the specified fire alarm system.

PART 2 - PRODUCTS

    - **********************************************************************************************

      - Seismic: If Project specification package includes Section << 26 0548.16 - Seismic Controls for Electrical Systems>>, and this Section includes devices that differ from those in Section << 26 0548.16 - Seismic Controls for Electrical Systems>> , then these products (i.e., the devices that differ) must be included in PART 2. And, if/when what’s been described is applicable, use the same terminology for these devices in PART 3 herein to identify the type of devices required for each application.

    - **********************************************************************************************

PERFORMANCE REQUIREMENTS

Provide materials and equipment that are new and unused, free of defects, specifically designed for the use intended, and are listed for use with the FACU.

Provide products suitable for operation at an elevation of 7,500 feet.

Where two or more products serving the same function are provided, they shall be exact duplicates produced by one manufacturer. (Note: Use of different models or options of products to achieve a system design requirement is not included in this requirement, e.g., weather-proof, conventional devices in exterior locations; or notification appliances with atypical output ratings that are better options for achieving design criteria).

      - ***************************************************************************************

      - Seismic: See Seismic Specification Editing Guide for editing guidance. If either paragraph in the Article below applies and there are too many systems/components to list here, then list them in an appendix to this section, and then add a reference to that appendix below.

      - ***************************************************************************************

SEISMIC PERFORMANCE REQUIREMENTS

The FACU components, raceways, or boxes, shall remain in place without separation of any parts when subjected to the design basis earthquake.

per Section ​​<< 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>​​​.

        - *** OR ***

as represented by the seismic forces derived from the criteria indicated ​​<< on the drawings; or  in Section  26 0548.16 - Seismic Controls for Electrical Systems>>​​.

The FACU components, raceway, or boxes, are Designated Seismic Systems and, as such, shall remain in place and be fully operational following the design basis earthquake.

per Section ​<< 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>​.

        - *** OR ***

as represented by the seismic forces derived from the criteria indicated << on the drawings; or  in Section  26 0548.16 - Seismic Controls for Electrical Systems>>.

MANUFACTURERS

Fire Alarm Control Units and Accessories

The FACU shall incorporate all control electronics and necessary components in a ​<< surface;  flush; or  semi-flush>>​ mounted cabinet. ​<< Design and install the FACU to meet ABA Standards , Section 307. ; or  None - N/A>>​​The cabinet with the operating controls and zone/supervisory indicators shall be located behind locked door with viewing window.

Provide sealed lead-acid batteries. Provide battery calculations when submitting the battery size.

Battery boxes, if required, shall be UL Listed for the purpose.

The system program shall meet the requirements of this project, applicable codes and standards, and satisfy the LANL Fire Protection Office.

Manufacturers:

          - **********************************************************************

          - Select only one of the two following subparagraphs.

          - **********************************************************************

Edwards Signaling Technologies (EST)

          - *** OR ***

Honeywell Security & Fire Solutions/Notifier

Initiating Devices and Notification Appliances

Same manufacturer as control units.

Provide initiating devices and notification appliances made by the same manufacturer, where possible.

Manufacturers:

          - **********************************************************************

          - Select any of the following Manufacturers, as applicable.

          - **********************************************************************

Honeywell Security & Fire Solutions/Notifier

Edwards Signaling Technologies (EST)

System Sensor

Wheelock

Kidde

Fike

Xtralis

PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; see Section << 01 2500 - Substitution Procedures>>.

For substitution of FACUs, submit product data showing equivalent features and compliance with Subcontract Documents.

For substitution of initiating devices and notification appliances, submit product data showing features and compliance with Subcontract Documents.

FIRE ALARM SYSTEM

Fire Alarm System: Provide << a new; or  modifications and extensions to the existing>> Fire Alarm system:

Provide all components necessary, regardless of whether shown in Subcontract Documents or not.

Comply with the following; where requirements conflict, order of precedence of requirements is as listed:

          - **********************************************************************

          - The following two subparagraphs are designer choices.

          - **********************************************************************

<<ADA Standards>> / <<ABA Standards>> in reference to Protruding Objects.

​<< DOE-STD-1066; or  _______>>​

Subcontract Documents (drawings and specifications).

<<NFPA 101>> and << ICC (IBC); or  ICC (IEBC)>>.

<<NFPA 72>>; where conflicts between requirements require deviation from <<NFPA 72>>, identify deviations clearly on design documents.

        - ******************************************************************************

        - The following five subparagraphs are designer choices.

        - ******************************************************************************

Evacuation Alarm: << Multiple smoke zones;  Allow for evacuation notification of any individual zone or combination of zones;  Single smoke zone; or  General evacuation of entire premises>>

Voice Notification: Provide emergency voice/alarm communications<< with multichannel capability;  _______; or  None - N/A>><< ; digital; or  None - N/A>>.

Program notification zones and voice messages as directed by FPO/AHJ.

Hearing Impaired Occupants: Provide visible notification devices in all public areas and in dwelling units.

Combined Systems: Do not combine fire alarm system with other non-fire systems.

FACU Spare Capacity

Initiating Device Circuits: Minimum 20 percent spare capacity of device count.

Notification Appliance Circuits: End of line voltage shall be greater than 17.6 VDC and have a 20 percent current capacity.

Speaker Amplifiers: Minimum 20 percent spare capacity of wattage.

Fire Alarm Control Units: Capable of handling all circuits utilized to capacity without requiring additional components other than plug-in control modules.

Power Sources – Primary and Secondary:

Primary: Dedicated branch circuits of the facility power distribution system.

Secondary Capacity: Provide batteries as represented in Article << 1.5; or  _______>> Design, subparagraph << 1.5.A.7; or  _______>> on Batteries.

Each Computer System: Provide uninterruptible power supply (UPS).

Seismic Qualification: Refer to Article ​<< 2.2; or  _______>>​ Seismic Performance Requirements. Include Special Certification from Manufacturer if Fire Detection and Alarm is a DSS.

FIRE SAFETY SYSTEMS INTERFACES

      - ***************************************************************************************

      - The following five paragraphs are designer choices.

      - ***************************************************************************************

Supervision: Provide supervisory signals in accordance with <<NFPA 72>>.

Alarm: Provide alarm initiation in accordance with <<NFPA 72>>.

Elevators: Provide alarm initiation in accordance with <<NFPA 72>> and <<ASME A17.1>>

HVAC: Provide alarm initiation in accordance with <<NFPA 72>> and <<NFPA 90A>>.

Doors: Provide alarm initiation in accordance with <<NFPA 72>> and <<NFPA 101>>.

      - ***************************************************************************************

      - The following eight Articles in PART 2 are designer choice based on project-specific requirements. Include based on fire alarm and detection system for project.

      - ***************************************************************************************

FACU COMPONENTS

For the Master List of Equipment approved by LANL, refer to Appendix A.

      - ***************************************************************************************

      - All paragraphs in this Article starting with Addressable Fire Alarm Control Unit (FACU) below are designer choices.

      - ***************************************************************************************

Addressable Fire Alarm Control Unit (FACU)

Basis of Design: Edwards Signaling Technologies; EST 4

        - *** OR ***

Basis of Design: Honeywell Security & Fire Solutions; Notifier Series; NFS2-640

Power Supply

The power supply shall be a high efficiency switch mode type with line monitoring. The automatic battery charger shall have low battery discharge protection. The power supply shall provide internal power and 24 VDC for notification appliance circuits. All outputs shall be power limited.

Digital Alarm Communicator Transmitter (DACT)

The FACU shall have a Digital Alarm Communicator Transmitter (DACT).

The DACT shall support dual telephone lines, “Contact ID” communications format, and configured for Dual-Tone, Multi-Frequency (DTMF).

The DACT shall be listed for “Central Station Fire Service” and for “Proprietary Station Fire Service” and shall be of the same manufacturer as the control panel.

FACU Panel Modules/Components

Provide an SLC Loop Controller for SLC for up to << 250;  500; or  318 more>> Devices.

For retrofit applications, provide an Initiating Device Circuit Module for existing Two-Wire, Normally Open Circuit Devices or Notification Devices:

FACU Cabinets

For smaller applications, the ​<< Single Chassis;  Two Tier; or  _______>>​ Cabinet shall be installed.

For larger applications, the ​<< Two Chassis;  Three-Tier; or  _______>>​ Cabinet shall be installed.

An approved equal based on the application.

High-Contrast, Alphanumeric Display and LED Indicators

Control Display Module (Disable Switch Card)

Graphic User Interface Computer Work Stations

Remote Annunciator Panel

Isolator Modules

Provide an Isolation Module for SLC configurations extending beyond a single zone as described in <<NFPA 72>>.

Synchronization Modules

Provide a Synchronization Output Module for NACs connected to a 24 VDC Riser.

Required for EST4 FACUs

Addressable Heat Detectors

The detector shall be temperature-rated at 135 degrees F (fixed temperature or rate-of-rise).

For applications requiring other than 135 degrees F, consult the LANL Fire Protection Office.

Addressable Photoelectric Detectors

Photoelectric Smoke Detectors shall be ceiling mounted or be suitable for wall mount applications where applicable.

Flame Detection

Listed for UV/IR capabilities

Carbon Monoxide Detectors

Gas Detectors: <<UL 2075>> listed and responsive to the sensitivity limits of <<UL 2034>>.

Combination Smoke/Carbon Monoxide Detectors

Combination Detectors, <<UL 1484>> or <<UL 2075>> listed.

Detector Mounting Bases

Standard bases suitable for mounting on 3-1/2 inch or 4 inch octagon box, or a 4 inch square box. The base shall contain no electronics and support all detector types. Removal of the detector shall not affect communications with other detectors.

Duct Smoke Detector

Provide duct housing assemblies for mounting an intelligent analog photoelectric detector along with a standard relay. Protect the measuring chamber from damage and insects. Provide an air exhaust tube and an air sampling inlet tube that extends into the duct air stream. Provide drilling templates and gaskets to facilitate locating and mounting the housing.

Provide duct detectors that are suitable for the air velocity and differential pressures measured for each air handling unit.

Beam Detectors

Addressable Manual Pull Stations

Provide Addressable Double-Action, Non-Coded Manual Pull Stations.

The fire alarm station shall be of Lexan or metal construction with an internal toggle switch. Provide a key locked feature. Finish the station in red with white PULL IN CASE OF FIRE lettering. The Manual Pull Station shall be suitable for mounting on 2-1/2 inch deep 1-gang boxes and 1-1/2 inch deep 4 inch square boxes with 1 gang covers.

Provide the appropriate back boxes and mounting plates for flush-mounting or surface mounting (depending on the building construction).

Addressable Control Relay Modules

Provide enhanced voltage and current ratings as appropriate for the application.

Addressable Monitor Modules

Provide Intelligent Single-Input or Dual-Input Modules as required to the addressable analog loop. Each input shall provide a supervised Class B Initiating Device Circuit.

Notification Appliances

Provide NRTL-listed 24 VDC audible, visual, and audible-visual combination-type electronic three-pulse temporal pattern horn sounder, strobe, and combination notification appliances.

Horns and Horn-Strobes shall be <<UL 464>> listed. For voice alarm systems, speakers shall be <<UL 1480>> listed. Horns and speakers shall be in a red housing.

Strobes and Horn-Strobes shall be <<UL 1971>> listed. Strobes shall have a xenon bulb or LED enclosed in a clear Lexan lens, and FIRE, in white lettering on a red trim plate or device housing.

Horns, Strobes, and Horn-Strobes shall mount to a 4 inch x 2-1/8 inch deep electrical box with single device cover. Provide weatherproof wall boxes for outdoor mounting.

Voice Evacuation Systems

Releasing

Notification Appliance Power Panels (NAPP)

Area of Refuge Emergency Two-Way Communication Systems (ECS)

Door Release

Refer to Section << 08 7100 - Door Hardware>> for door hardware requirements.

Air-Sampling Smoke Detection Systems

<< Design and provide;  Provide; or  _______>>​ smoke detection system suitable for application and coverage area indicated, consisting of smoke detector unit with aspirator/fan that continuously draws air into sensing chamber through connected sampling pipe network and associated sampling ports.

Comply with <<NFPA 72>> and list and label as complying with <<UL 268>>.

Comply with applicable requirements of <<NFPA 76>> for << Very Early Warning Fire Detection (VEWFD);  Early Warning Fire Detection (EWFD);  Standard Fire Detection (SFD); or  _______>>.

Use manufacturer's recommended sampling pipe and fittings; plenum rated; identified in accordance with <<NFPA 72>>.

Design using manufacturer's product-specific design software or based on manufacturer's pre-engineered design suitable for the application.

Xtralis: VESDA Aspirating Smoke Detection.

RACEWAYS

Refer to Section << 26 0533 - Raceways and Boxes for Electrical Systems>>, for raceway systems.

All interior fire alarm raceways for power-limited circuits shall be red EMT, unless otherwise approved.  Note: Fittings, conduit bodies, junction boxes, and device boxes are not required to be red.

Minimum raceway size shall be 3/4 inch, unless otherwise approved.

All EMT raceway fittings shall be compression type.

      - ***************************************************************************************

      - The following five paragraphs are designer choices.

      - ***************************************************************************************

One-half (1/2) inch FMC up to 6 feet in length is allowed in between addressable modules and controlled and monitored devices.

Provide IMC or RMC for exposed outdoor raceways, when subject to damage.

Provide PVC, tape-wrapped IMC, RTRC, or tape-wrapped RMC for underground work.  Note: Must be installed per manufacturer recommendations.

Raceways for 120 VAC circuits shall be unpainted galvanized.

If red exterior fire alarm raceway is not readily available, it is permitted to instead apply outdoor rated UV resistant “Fire Alarm” labels at 10 feet intervals.

JUNCTION BOXES AND BACKBOXES

Refer to Section << 26 0533 - Raceways and Boxes for Electrical Systems>>, for junction boxes.

WIRING

New wiring shall be provided unless re-use of existing has been approved.

Color Code fire alarm wiring as follows:

| Black, Red, or Blue | 120 VAC (Ungrounded Conductor – Match Existing) |
| --- | --- |
| White | 120 VAC Neutral Wire (Grounded Conductor) |
| Green | Equipment Grounding Conductor |
| Blue (-) / Yellow (+) | Negative/Positive Connection for Notification Appliance Circuits |
| Gray (-) / Violet (+) | Negative/Positive Conventional Alarm IDC |
| Black (-) / Red (+) | Negative/Positive Auxiliary Circuit Connections |
| Black (-) / Red (+) T/S | Negative/Positive for SLC or Speaker Circuit |

Refer to manufacturer specifications for telephone wire color configuration (four-pair wire method) for both DACT lines.

Conductors: Minimum Requirements:

Interior/Dry Locations: Red-jacketed << FPL; or  FPLR>> cable << shielded; or  non-shielded>> with No. 16 AWG (minimum) twisted-pair conductors for SLC and listed per <<UL 1424>>.

Minimum No. 14 AWG THHN/THWN-2 for NAC, AUX, and IDC.

Low voltage binary signal conductors shall be type TFN/AWM, No. 16 AWG minimum, and solid copper conductor. For sizes larger than No. 16 AWG, use THHN/THWN-2.

Other low voltage conductors shall be type TFN/AWM, No. 16 AWG (minimum), solid copper conductor. For sizes larger than No. 16 AWG, use THHN/THWN-2.

        - ******************************************************************************

        - The following subparagraph is a designer choice and applies to exterior/wet locations.

        - ******************************************************************************

Exterior/Wet Locations: Red or Black-jacketed FPL/PLTC cable, No. 16 AWG (minimum), twisted-pair conductors for SLC, and listed for WET locations per <<UL 1424>>.

West Penn Catalog #AQ225 for SLC, or an approved equal.

Minimum No. 14 AWG unshielded for NAC, AUX, and IDC.

Low voltage binary signal conductors: TFN/AWM, No. 16 AWG minimum, and solid copper conductor.

Power conductors: Type THHN/THWN-2, No. 12 AWG, thermoplastic insulation, and single solid copper conductor.

TEST EQUIPMENT

Provide any special test equipment manufactured by the fire alarm equipment manufacturer for maintenance, testing, or troubleshooting.

All test equipment shall be calibrated and provided with a calibration certificate.

SURGE PROTECTION DEVICES (SPD)

      - ***************************************************************************************

      - The following three paragraphs are designer choices.

      - ***************************************************************************************

Provide a <<UL 1449>> listed 120 VAC surge protective device for the main FACU, sub-FACUs, and each Notification Appliance Power Supply (NAPP) that have a 120 VAC supply circuit.

Device shall be capable of absorbing a maximum single pulse of at least 6,500A.

Manufacturer: DITEK-120SRD

Provide <<UL 497B>> listed surge protective devices for each analog and 24 VDC initiating device signaling circuits, 24 VDC control circuits, and 24 VDC notification appliances entering/leaving each building that is monitored by the FACU.

Devices shall be capable of absorbing a peak 8x20 microsecond current of not less than 10,000A for 24 VDC initiating devices & control circuits and 10,000A for analog initiating devices, at least 10 times.

Devices for notification appliances shall be capable of absorbing a peak 8x20 microsecond current of 5000A and a 2000A occurrence at least 50 times.

Protective device for notification appliances shall have a series resistance not exceeding 0.2 ohms per pair and shall be capable of carrying a continuous current of 5A.

Clamping voltage shall not exceed 30 volts for initiating devices control circuits, and 43 volts for notification appliances.

Capacitance shall not exceed 50 pf for analog initiating devices.

Provide matching receptacle for plug-in surge protective devices.

Manufacturer: DITEK-DTK-2MHLP Series

Provide a <<UL 497B>> listed four-wire surge protective device for each FACU RS-232 & RS-485 circuits entering/leaving each building monitored by the FACU.

Device shall be capable of absorbing a peak 8x20 microsecond current of 10,000A at least 10 times.

Clamping voltage shall not exceed 20 volts for RS-232 applications and 8 volts for RS-485 applications.

Line-to-line and line-to-ground capacitance for RS-485: 50 pf maximum.

MANUAL TRANSFER SWITCH

Manufacturers:

        - ******************************************************************************

        - Select only one of the two following subparagraphs.

        - ******************************************************************************

Reliance Pro/Tran Signa C20A1N

Reliance Model Easy/Tran CSR201

PANEL RECEPTACLES

125-volt NEMA-5-15R duplex receptacle. Refer to Section << 26 2726 - Wiring Devices>>.

PART 3 - EXECUTION

    - **********************************************************************************************

      - Seismic: If Project specification package includes Section ​<< 26 0548.16 - Seismic Controls for Electrical Systems>>​, and this section includes requirements associated with installation, testing, and inspection of mounting and/or anchorage devices that differ from those in Section ​<< 26 0548.16 - Seismic Controls for Electrical Systems>>​, then the differing requirements must be included in PART 3 herein.

    - **********************************************************************************************

GENERAL

Installation shall not proceed without 100 percent design package approval by the Fire Protection Office.

Prior to installation, carefully inspect the installed work of other trades, whether pre-existing or part of this project and verify that such work is complete to the point where the installation of the fire alarm system may properly commence.

Notify the << LANL STR; or  LANL PE>> if conditions exist, not resulting from work of this project, that prohibit the installation from conforming to applicable codes, regulations, standards, and the original, approved design.

Coordinate installation of fire alarm system with work of other trades.

Coordinate installation of ceiling mounted fire alarm devices and associated equipment with existing ceiling or roof materials, lighting, ductwork, raceways, piping, suspended equipment, structural and other building components.

Verify dimensions in the field to lay out work in the most direct and expeditious manner and avoid interference.

Locate notification appliances away from obstructions and notify the << LANL STR; or  LANL PE>> of possible obstruction by other trades, equipment, or furnishings.

Protect fire alarm equipment with suitable coverings until completion of project.

Coordinate necessary shutdowns of existing systems by notifying the << LANL STR; or  LANL PE>> a minimum of seven working days before rendering such systems inoperative. Do not render inoperative any system without the prior approval of the << LANL STR; or  LANL PE>>.

INSTALLATION

Install in accordance with <<NFPA 72>>, <<NFPA 70>>, <<NECA 305>>​, Subcontract Documents, and this Section.

Coordinate necessary shutdowns of existing systems by notifying the << LANL STR; or  LANL PE>> a minimum of seven working days before rendering such systems inoperative.

Do not render inoperative any system without the prior approval of the << LANL STR; or  LANL PE>>. The << LANL STR; or  LANL PE>>​ will submit Form 1821 - Utility Outage (LANL access only).

      - ***************************************************************************************

      - Seismic: If some of the components in the FACU are exempt, then Sections << 26 0529 - Hangers and Supports for Electrical Systems>> and << 26 0548.16 - Seismic Controls for Electrical Systems>>—or << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>—are applicable. Regarding the applicability of Section << 26 0548.16 - Seismic Controls for Electrical Systems>> or << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>, see Seismic Specification Editing Guide for editing guidance.

      - ***************************************************************************************

Follow Section << 26 0529 - Hangers and Supports for Electrical Systems>><< and Section 26 0548.16 - Seismic Controls for Electrical Systems;  and, if applicable, Section  01 8734 - Seismic Qualification of Nonstructural Components (IBC); or  None - N/A>> for anchorage requirements.

Install fire alarm devices to be serviceable, unless unfeasible due to required installation location (e.g., above-ceiling smoke detectors).

      - ***************************************************************************************

      - The following paragraph is a designer choice and applies to Monitor Modules, Control Relays, and Remote Alarm Indicators.

      - ***************************************************************************************

Install Monitor Modules, Control Relays, and Remote Alarm Indicators:

Between 60 inches and 72 inches AFF.

If the Control Circuit is not Class A, Style D, then it shall be within 3 feet (nominal) of the monitored equipment or emergency control function, unless approved otherwise by FPO.

All fire alarm equipment requiring servicing or maintenance shall have a minimum clear working space of 36 inches by 36 inches, or as wide as the equipment, centered on the equipment. The clear height of the working space shall be 72 inches, or the height of the equipment if more than 72 inches. The clear working space shall be in a routinely accessible location as approved by the LANL Fire Protection Office.

      - ***************************************************************************************

      - Select the following two paragraphs as applicable to the project.

      - ***************************************************************************************

Replacement Projects: Remove existing system completely after new system is fully operational and tested.

Modification Projects: Remove existing components indicated and incorporate remaining components into new system, under warranty as if they were new; do not take existing portions of system out of service until new portions are fully operational, tested, and connected to existing system.

      - ***************************************************************************************

      - The following three paragraphs are designer choices and apply to replacement/modification projects.

      - ***************************************************************************************

Clearly label components that are "Not in Service."

Remove unused existing components and materials from site and dispose of properly after coordination with FPO or LANL STR.

Remove abandoned cables and raceways. Tag raceways that are for future use.

      - ***************************************************************************************

      - The following Article is a designer choice and applies to power supply and MTS.

      - ***************************************************************************************

POWER

Install 120 VAC manual transfer switch (MTS) in FACU/NAPP branch circuit before the power SPD.

Install MTS so that it is readily accessible above or adjacent to the FACU/NAPP. The transfer switch shall be located before the AC surge suppressor.

Install a 125-volt NEMA-5-15R duplex receptacle below each FACU/NAPP. Provide dedicated circuit from a panel that does not power the FACU/NAPP. Refer to Section << 26 2726 - Wiring Devices>>.

      - ***************************************************************************************

      - The following Article is a designer choice and applies to FACU and NAPP installation.

      - ***************************************************************************************

FACU AND NAPP INSTALLATION

Install FACU or NAPP following manufacturer’s written instructions, <<NFPA 72>>, and <<NFPA 70>>.

Locate the FACU in the main building lobby or entry vestibule, if a conditioned space. Coordinate location of FACU with the LANL Fire Protection Office.

Unless otherwise approved, install FACU or NAPP with top of cabinet trim 66 inches AFF.

Mount FACU or NAPP cabinet plumb and rigid without distortion of the box.

Mount flush cabinets uniformly flush with wall surfaces.

Install filler plates in unused spaces in FACU or NAPP.

Train conductors in cabinet gutters neatly in groups; bundle and wrap with cable ties after completion of testing.

Tighten electrical connectors and terminals, including grounding connections, according to the manufacturer’s published torque-tightening values (typically marked on the equipment). Where manufacturer values cannot be located, contact the manufacturer for guidance.

      - ***************************************************************************************

      - The following Article is a designer choice and applies to wiring installation.

      - ***************************************************************************************

WIRING INSTALLATION

Install all fire alarm system and power wiring in raceways.

      - ***************************************************************************************

      - The following paragraph is a designer choice.

      - ***************************************************************************************

Do not install AC current-carrying conductors in the same raceway with the DC or digital fire alarm detection and signaling conductors.

Underground raceways shall be swabbed prior to installing respective conductors.

Do not pull wire or cable until the raceway system is complete between pull points.

Bundle conductors in panels and boxes into groups by service and destination.

Run electronic cable continuous between device termination points. No splicing is permitted without prior approval from the Fire Protection Office.

Where splicing is approved:

Provide “Wago” Splicing Connectors or Terminal Blocks/Strips.

Wire nuts shall not be used.

Adhere to the manufacturer requirements/limitations for T-taps. Make no T-taps in notification appliance circuits. T-taps shall only be made on device terminals or on terminal strips that are acceptable to the Fire Protection Office. Wire nuts are not approved and shall not be used.

Make allowances in conductor length at panels and other enclosures to permit forming the conductors neatly within the enclosures.  Where wiring troughs are not provided with the enclosures, neatly cable and adequately support the wiring.

Plan for additional wires required during pulls, such as ground conductors for SPDs.

      - ***************************************************************************************

      - The following paragraph is a designer choice.

      - ***************************************************************************************

Ring out and identify power and control conductors before terminal connections are made.

Check polarity and phasing and make changes as required before making terminal connections.

Test conductors for continuity and presence of shorts and unintentional grounds.

Utilize Fire Alarm Terminal Cabinets (FATC) where needed, with approval from FPO.

      - ***************************************************************************************

      - Include the following two Articles only when applicable to the project.

      - ***************************************************************************************

JUNCTION BOX AND RACEWAY INSTALLATION

Refer to Section ​<< 26 0533 - Raceways and Boxes for Electrical Systems>>​, for junction box and raceway installation requirements.

SURGE PROTECTIVE DEVICE INSTALLATION

Install a 120 VAC SPD for the FACU, NAPP, and any other AC power supplies.

Install an SPD for each dedicated IDC, NAC, data, and SLC entering/extending beyond each building.

SPDs shall be installed between 44 inches and 72 inches AFF.

Install FACU 120VAC SPDs in one or more metal enclosures near the protected Fire Alarm Control Unit.

Provide separate or divided enclosures for 120 VAC Power and Low Voltage Device SPDs.

Install a single-point ground bar in the 120 VAC SPD Enclosure:

Bond the Ground Bar to the enclosure and the power circuit equipment-grounding conductor.

Connect each SPD to the Ground Bar with a separate 12 AWG solid, green-insulated ground wire.

12 AWG Ground Wire shall be routed back to the FACU or Fire Auxiliary Power Supply in a raceway.

Install SPDs in accordance with manufacturer’s instructions, keeping leads and ground conductors as short and straight as possible.

Provide matching receptacle for plug-in surge protective devices.

IDENTIFICATION

Follow Section << 26 0553 - Identification for Electrical Systems>>, for all system components.

For field labelling purposes, FACU is the required acronym.

Provide pressure-sensitive, vinyl labels with red lettering of 3/4 inch (minimum) on a white background, unless otherwise noted below.

Inside the FACU and NAPP, all devices shall be labeled, and all zone locations shall be clearly identified.

Label each conductor at each terminal point:

Use wire markers specified in Section << 26 0553 - Identification for Electrical Systems>>.

On wire markers indicate the type of fire alarm circuit. SLC circuits shall be identified by the loop number indicated on the riser diagram (e.g. SLC-1, etc.).

NAC circuits shall be identified by the source and circuit number indicated on the riser diagram (e.g., NAPP1-1, FACU1-2, etc.).

Auxiliary system circuits shall be identified by component ID of the interfaced system and the prefix FA (e.g., FA BAS-PNL-001, FA HVA-001, etc.).

Label fire alarm and branch circuit junction boxes and conduit bodies with FIRE ALARM on a 2-1/4 inches x 1/2 inch (minimum size) label.

Label junction boxes containing terminal blocks with FIRE ALARM – TERMINAL BLOCK on a 2-1/4 inches x 1/2 inch (minimum size) label.

Label all devices with address/zone information as shown on the drawings.

Label device settings on adjustable devices (Candela, Temperature, Delay Time, Wattage, Alarm Thresholds, etc.).

Provide red markings and a locking mechanism on branch circuit breakers and other disconnecting means.

Identify fire alarm equipment on electrical panel schedules and terminal cabinet schedules (“Fire Alarm”, “Emergency Communication System”).

Label the MTS with the electrical panel and circuit number of the feeding branch circuit, and “For Fire Alarm Panel Use Only. ​<< For Use with Non-Bonded Portable Generator” on a 2-1/4 inch x 1/2 inch (minimum size) label. Keep only if using existing type, when using the CSR201.; or  None - N/A>>​

Remove abandoned cables and conduits. Tag conduits that are for future use.

      - ***************************************************************************************

      - Painting is at the direction of the FOD (based on aesthetics, environmental conditions, etc.). If not required by FOD, omit the following article and any other references to painting in this document.

      - ***************************************************************************************

PAINTING

For painting, refer to Section << 09 9100 - Painting>>.

Exposed Surfaces: Paint/patch and clean exposed walls that were affected by the installation/demolition, with an approved matching paint.

Refinishing: Thoroughly clean and touch up shop-primed or finish-painted surfaces damaged in installation with an approved matching paint.

EQUIPMENT INSTALLATION

Install devices or equipment not specifically covered by this Section in accordance with manufacturer's instructions.

      - ***************************************************************************************

      - The following Article is a designer choice and applies to connections to LANL Proprietary Supervising Station.

      - ***************************************************************************************

CONNECTION TO LANL PROPRIETARY SUPERVISING STATION

Install 6 inches x 6 inches x 4 inches electrical enclosure adjacent to the FACU with a raceway to the appropriate factory knockout.

Install a 1 inch raceway, with a measuring pull tape, from the electrical enclosure to the backboard located in the main telecom room.

Install three (3) red GFE Category 6A cables in the raceway.

Route two (2) Cat 6A cables to the building’s telephone terminal board.

Route the third Cat 6A cable to the nearest open network switch in the building. Coordinate with the LANL Telecommunication Services Group (NIE-TS) to ensure proper location.

CLEANING

Blow out junction boxes and fire alarm equipment not hermetically sealed with clear, dry, oil-free (15 psig maximum) air to remove dust prior to energizing.

FIELD QUALITY CONTROL

      - ***************************************************************************************

      - Note: Testing and commissioning of fire alarm systems is a three-step process at LANL. First the installing Subcontractor performs quality control inspections and testing, and any required corrections. A Statement of Compliance and/or a Preliminary Test Report (if required) is to be provided to LANL, along with revised drawings and the current FACU program.

      - Next a LANL-supported, pre-final test is performed to verify correct DACT signals reporting to the LANL supervising station at the EOC. Changes made after the pre-final test will require sufficient time to make changes to LANL supervising station account.

      - Finally, the LANL-supported final acceptance test is performed.

      - ***************************************************************************************

The Subcontractor’s Qualified Fire Alarm Technician or Installer shall ensure the completeness and correctness of the installation by performing the following quality assurance check:

Field-verify and red-line installation/design drawings of fire alarm layout, raceway and wiring plans, and point-to-point field-wiring diagrams.

Verify correct labeling of fire alarm system conductors.

Verify correct conductor sizes.

Update calculations to reflect field changes.

Verify audible alarm in all spaces meets design sound pressure levels.

Test all devices for proper supervision and alarm operation.

Test all emergency interfaces with for proper operation in all modes.

Perform preliminary inspection and testing of the fire alarm system.

Prepare test plan and report.

Prepare as-built (record) drawings.

PRE-FINAL AND FINAL ACCEPTANCE TESTS

Coordinate date of pre-final and final acceptance tests with installer, << LANL STR; or  LANL PE>>​, LANL Fire Protection Office representative, and sub-tier Subcontractors for HVAC, Sprinklers, Elevator Controls, and all other interfaced systems.

Requests for pre-final or final acceptance tests shall not be made before approval of the 100 percent design documentation.

Notify << LANL STR; or  LANL PE>> at a minimum of 10 working days in advance of LANL-supported pre-final and final acceptance tests. For large projects, notification shall be based on a timeline approved by the LANL Fire Protection Office.

The following shall be provided with the request for LANL-supported pre-final and final acceptance test:

Revised versions of the FACU Program, Centration Station Reports, or Input/Output Matrix.

Marked-up (red-lined) shop drawings and point-to-point wiring diagrams.

Approved final test plan.

        - ******************************************************************************

        - The following two subparagraphs are designer choices.

        - ******************************************************************************

Statement of Compliance.

The Installer's Preliminary test Report, indicating the status of the fire alarm system and any corrective actions required.

Perform pre-final and final acceptance tests on the completed fire alarm system:

Perform final tests in the presence of authorized representatives of << LANL STR; or  LANL PE>>, Fire Protection Office, and Facility Operations Director (FOD).

Follow the approved test plan and comply with <<NFPA 72>> and <<NECA 305>> requirements.

Perform end-to-end, integrated testing for the entire system.

LANL will perform 24-hour discharge test on the FACU/NAPP batteries.

Startup and Commissioning Group will measure air velocity and pressure differentials in ducts.

LANL will perform tests on connections made by other LANL groups.

LANL Telecommunication Services Group (ISD-TS) will perform the acceptance test of the telephone lines from the modular plug connectors.

Re-verify the complete fire alarm raceway and wiring system in the presence of a LANL Fire Protection Office representative, upon request.

Correct deficiencies discovered in the final acceptance test and re-test fire alarm system until satisfactory test results are obtained.

      - ***************************************************************************************

      - The following Article is a designer choice related to FACUs as described below.

      - ***************************************************************************************

SIGNAGE

For FACUs located other than inside the entry vestibule, furnish and install a permanently mounted placard in or adjacent to the fire alarm control cabinet that can withstand the environmental conditions at the panel.

Provide the following information typewritten or engraved on the placard:

Location of Fire Alarm Control Unit.

END OF MAIN SECTION; Appendix follows

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

  - THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

  - THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 28 4600, REV. 6, DATED APRIL 15, 2026.

    - Appendix A – Master Equipment List Reference

      - List of equipment approved by LANL FPO/AHJ. For equipment not listed, seek approval from the FPO/AHJ.

| ​ POWER SUPPLIES |  |  |
| --- | --- | --- |
| ​ FACU COMPABILITY | ​ PART NUMBER | ​ DESCRIPTION |
| Edwards | EST 4-PPS/M | - |
| Notifier | ACPS-610 | - |

| ​ DIGITAL ALARM COMMUNICATOR TRANSMITTER (DACT) |  |  |
| --- | --- | --- |
| ​ FACU COMPABILITY | ​ PART NUMBER | ​ DESCRIPTION |
| Edwards | 3-MODCOM | - |
| Notifier | UDACT-2 | - |

| ​ FACU PANEL MODULES/COMPONENTS |  |  |
| --- | --- | --- |
| ​ FACU COMPABILITY | ​ PART NUMBER | ​ DESCRIPTION |
| Edwards | 3-SSDC2 | Single Signature Driver Controller |
|  | 3-SDDC2 | Dual Signature Driver Controller |
| Notifier | LEM-320 | Loop Expander Module |

| ​ FACU PANEL MODULES/COMPONENTS |  |  |
| --- | --- | --- |
| ​ FACU COMPABILITY | ​ PART NUMBER | ​ DESCRIPTION |
| Edwards | 3-IDC8/4 | Initiating Device Circuit Module |
| Notifier | XP10-M(A) | Ten-Input Monitor Module |

| FACU CABINETS |  |  |
| --- | --- | --- |
| FACU COMPABILITY | PART NUMBER | DESCRIPTION |
| Edwards | 3-CAB7B | Single Chassis Backbox, Black |
|  | 4-CAB16DR | Single Chassis Door Assembly, Red |
|  | 3-CAB14B | Two Chassis Backbox, Black |
|  | 4-CAB24DR | Two Chassis Door Assembly, Red |
| Notifier | CAB-4 “B” | Two-Tier Backbox, Black |
|  | DR-B4R | Two-Tier Door Assembly, Red |
|  | CAB-4-“C” | Three-Tier Backbox, Black |
|  | DR-C4R | Three-Tier Door Assembly, Red |

| FACU DISPLAYS |  |  |
| --- | --- | --- |
| FACU COMPABILITY | PART NUMBER | DESCRIPTION |
| Edwards | 4-LCDLE | Color LCD Display |
| Notifier | KDM-R2 | LCD Display |

| CONTROL DISPLAY MODULE (DISABLE SWITCH CARD) |  |  |
| --- | --- | --- |
| FACU COMPABILITY | PART NUMBER | DESCRIPTION |
| Edwards | 4-24L12S | 24 Indicator, 12 Control Display Module |
| Notifier | ACM-24AT | 24-Programable Buttons, Annunciator Control Module |

| GRAPHIC USER INTERFACE COMPUTER WORKSTATION |  |  |
| --- | --- | --- |
| FACU COMPABILITY | PART NUMBER | DESCRIPTION |
| Edwards | FW-UL6SWW10 | Fireworks – Server Workstation |
|  | FW-CGS | Fireworks - Software |
| Notifier | OW-SWKIT-US-3 | ONYXWorks |

| ​ REMOTE ANNUNCIATOR PANEL |  |  |
| --- | --- | --- |
| ​ FACU COMPABILITY | ​ PART NUMBER | ​ DESCRIPTION |
| Edwards | 4-2ANN | Color Touch Screen Annunciator |
|  | 4-2ANNMT | 4-2ANN Backbox |
| Notifier | LCD2-80 | LCD Annunciator |
|  | ABF-1DB(C) | LCD2-80 – Semi-Flush Box with Door and Keylock |

| ​ ISOLATOR MODULES |  |  |
| --- | --- | --- |
| ​ FACU COMPABILITY | ​ PART NUMBER | ​ DESCRIPTION |
| ​ Edwards | SIGA-IM2 | Fault Isolator Module |
|  | SIGA-SB4 | Standard Detector Isolator Base |
| ​ Notifier | ISO-X-(A) | Fault Isolator Module |
|  | SMB500 | ISO-X-(A) Surface Mount Backbox |
|  | B22BI-WH | Standard Detector Isolator Base |

| ​ SYNCHRONIZATION MODULES |  |  |
| --- | --- | --- |
| ​ FACU COMPABILITY | ​ PART NUMBER | ​ DESCRIPTION |
| ​ Edwards | SIGA-CC1S | Synchronization Output Module |

| ​ ADDRESSABLE HEAT DETECTORS |  |  |
| --- | --- | --- |
| ​ FACU COMPABILITY | ​ PART NUMBER | ​ DESCRIPTION |
| ​ Edwards | SIGA-HFD | Fixed Temperature |
|  | SIGA-HRD | Rate-of-Rise |
|  | EST 302 Series | Hazardous Locations |
| ​ Notifier | FST-951 | Fixed Temperature |
|  | FST-951R | Rate-of-Rise |
|  | Thermotech EPM Series | Hazardous Locations |
| ​ Conventional | Fike 60-1029 | Rate-of-Rise/Fixed Temperature |
|  | System Sensor Series 100 | Rate-of-Rise/Fixed Temperature |

| ​ ADDRESSABLE PHOTOELECTRIC DETECTORS |  |  |
| --- | --- | --- |
| ​ FACU COMPABILITY | ​ PART NUMBER | ​ DESCRIPTION |
| Edwards | SIGA-OSD | - |
| Notifier | FSP-951 | - |
| Conventional | System Sensor 2W-B | - |
|  | Fike 63-1024 | - |
|  | 30-3013 | Hazardous Location |

| ​ FLAME DETECTION |  |  |
| --- | --- | --- |
| FACU COMPABILITY | PART NUMBER | DESCRIPTION |
| Notifier | Fire Sentry Series | - |

| ​ CARBON MONOXIDE DETECTORS |  |  |
| --- | --- | --- |
| ​ FACU COMPABILITY | PART NUMBER | DESCRIPTION |
| Edwards | SIGA-COD | - |
| Notifier | FSCO-951 | - |

| COMBINATION SMOKE/CARBON MONOXIDE DETECTORS |  |  |
| --- | --- | --- |
| FACU COMPABILITY | PART NUMBER | DESCRIPTION |
| Edwards | SIGA-OSCD | - |
| Notifier | FPC-951(A) | Standard Detector Isolator Base |

| ​ DETECTOR MOUNTING BASES |  |  |
| --- | --- | --- |
| ​ FACU COMPABILITY | ​ PART NUMBER | ​ DESCRIPTION |
| Edwards | SIGA-SB4 | - |
| Notifier | B300-6 | Low Profile Base |

| ​ DUCT SMOKE DETECTOR |  |  |
| --- | --- | --- |
| ​ FACU COMPABILITY | ​ PART NUMBER | ​ DESCRIPTION |
| Edwards | SIGA-SDH | With SIGA-OSD |
|  | SIGA-LED | Remote Alarm LED |
|  | SD-T Series | Sampling Tubes |
| Notifier | DNR(A) | With FSP-951R |
|  | DNRW | With FSP-951R |
|  | RA100Z | Remote Alarm LED |
|  | DST Series | Sampling Tubes |
| Conventional | Fike 63-029 | - |
|  | System Sensor InnovairFlex | - |

| ​ BEAM DETECTORS |  |  |
| --- | --- | --- |
| ​ FACU COMPABILITY | ​ PART NUMBER | ​ DESCRIPTION |
| Edwards | EST EC3000 | - |
| Notifier | FS-OSI-RI | - |

| ​ ADDRESSABLE MANUAL PULL STATIONS |  |  |
| --- | --- | --- |
| ​ FACU COMPABILITY | ​ PART NUMBER | ​ DESCRIPTION |
| Edwards | SIGA-278 | Pull Stations |
|  | 276B- RSB | Backboxes |
|  | 278A-REL | Releasing Pull Station |
|  | RELA-ABT | Releasing Abort Switch |
|  | EST MPSR2 Series | Hazardous Locations |
|  | FIKE 10-2963 | Hazardous Locations |
| Notifier | NBG-12LX | Pull Stations |
|  | SB-10 | Backboxes |
|  | NBG-12LRAA | Pull Station & Abort Switch |
|  | FIKE 10-2963 | Hazardous Locations |

| ​ ADDRESSABLE CONTROL RELAY MODULES |  |  |
| --- | --- | --- |
| ​ FACU COMPABILITY | ​ PART NUMBER | ​ DESCRIPTION |
| Edwards | SIGA-CR | - |
|  | SIGA-CRH | - |
| Notifier | FRM-1 | - |

| ​ ADDRESSABLE MONITOR MODULES |  |  |
| --- | --- | --- |
| ​ FACU COMPABILITY | ​ PART NUMBER | ​ DESCRIPTION |
| Edwards | SIGA-CT1 | Single-Input Module |
|  | SIGA-CT2 | Dual-Input Module |
|  | SIGA-UM | Class A Configurations |
|  | SIGA-REL | Releasing Control Module |
| Notifier | FMM-1 | FlashScan Monitor Module |
|  | FDM-1 | FlashScan Dual Monitor Module |
|  | FCM-1-REL | Releasing Control Module |

| ​ NOTIFICATION APPLIANCES |  |  |
| --- | --- | --- |
| ​ FACU COMPABILITY | ​ PART NUMBER | ​ DESCRIPTION |
| Edwards | EST Genisis Series | - |
|  | WHEELOCK Eluxa Series | - |
|  | System Sensor LED Series | - |
|  | Protocol Dependent, Selection on Approval | Hazardous Location Strobe |
|  |  | Hazardous Location Horn Strobe |
| Notifier | WHEELOCK Eluxa Series | - |
|  | System Sensor LED Series | - |
|  | Protocol Dependent, Selection on Approval | Hazardous Location Strobe |
|  |  | Hazardous Location Horn Strobe |

| ​ VOICE EVACUATION SYSTEMS |  |  |
| --- | --- | --- |
| ​ FACU COMPABILITY | ​ PART NUMBER | ​ DESCRIPTION |
| Edwards | EST Genesis Series | With approved Backbox |
| Notifier | System Sensor SpectrAlert Series | With approved Backbox |
|  | System Sensor SpectreAlert Series | With approved Backbox |

| ​ RELEASING |  |  |
| --- | --- | --- |
| ​ FACU COMPABILITY | ​ PART NUMBER | ​ DESCRIPTION |
| Edwards/Notifier | WHEELOCK Eluxa Series | Horns |
|  | WHEELOCK Eluxa Series | Strobes with Clear, Amber, Red, or Blue Lenses |
|  | WHEELOCK ELSBB-R | Backbox |

| ​ NOTIFICATION APPLIANCE POWER PANEL (NAPP) |  |  |
| --- | --- | --- |
| ​ FACU COMPABILITY | ​ PART NUMBER | ​ DESCRIPTION |
| Edwards | BPS-10A | - |
| ​ Notifier | ACPS-610 | - |

| ​ AREA OF REFUGE EMERGENCY TWO-WAY COMMUNICATION SYSTEMS (ECS) |  |  |
| --- | --- | --- |
| ​ COMPONENTS | ​ PART NUMBER | ​ DESCRIPTION |
| Central Control Point | RATH SmartRescue Base Stations | 2500-205 |
|  |  | 2500-210 |
| Remote Call Stations | RATH 2100-986 | - |
|  | ALPHAREFUGE RCB2100 Series Callbox | - |
| Power Supply | RATH 2500-PWR24U | Contacts for Power Failure Supervision |
|  | AlphaRefuge PWR2410A | If Central Control Point is not Remote Powered |

| ​ DOOR RELEASE |  |  |
| --- | --- | --- |
| ​ FACU COMPABILITY | ​ PART NUMBER | ​ DESCRIPTION |
| Edwards | EST Electromagnetic Door Holders | - |

END OF SECTION