Section 33 1000 
Water Utilities

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 10 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Civil POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable specification sections from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality sections.

  - *************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

Site water distribution piping system (potable and fire water) beyond the building wall.

        - ******************************************************************************

        - The following subparagraphs are designer choices based on project-specific requirements.

        - ******************************************************************************

Flanges, Unions, and Couplings

Valves, Above Grade

Valves, Below Grade

Water Pressure Reducing Valves (PRV)

Fire Hydrants

Post Indicators

Backflow Preventer

Pressure Gauge

Service Saddle

Tapping Sleeve

Valve Box

related requirements

Section << 01 2500 - Substitution Procedures>>

Section << 01 3300 - Submittal Procedures>>

Section << 01 4444 - Offsite Welding, Brazing and Joining Requirements>>​

Section << 01 4455 - Onsite Welding, Brazing and Joining Requirements>>

Section << 22 0554 - Identification for Plumbing,  HVAC, and Fire Piping and Equipment>>

Section << 22 0813 - Testing Piping Systems>>

Section << 22 0816 - Disinfection of Potable Water Piping>>

Section << 31 2000 - Earth Moving>>

reference standards

ASME B16.22 - Wrought Copper and Copper Alloy Solder-Joint Pressure Fittings.

ASME B16.42 - Ductile Iron Pipe Flanges and Flanged Fittings: Classes 150 and 300.

ASME B40.100 - Pressure Gauges and Gauge Attachments.

ASSE 1013 - Performance Requirements for Reduced Pressure Principle Backflow Prevention Assemblies.

ASSE 1047 - Performance Requirements for Reduced Pressure Detector Backflow Prevention Assemblies.

ASTM B88 - Standard Specification for Seamless Copper Water Tube.

ASTM D3035 - Standard Specification for Polyethylene (PE) Plastic Pipe (DR-PR) Based on Controlled Outside Diameter.

ASTM D3139 - Standard Specification for Joints for Plastic Pressure Pipes using Flexible Elastomeric Seals.

ASTM D3261 - Standard Specification for Butt Heat Fusion Polyethylene (PE) Plastic Fittings for Polyethylene (PE) Plastic Pipe and Tubing.

ASTM D3350 - Standard Specification for Polyethylene Plastics Pipe and Fittings Materials.

ASTM F477 - Standard Specification for Elastomeric Seals (Gaskets) for Joining Plastic Pipe.

ASTM F714 - Standard Specification for Polyethylene (PE) Plastic Pipe (DR-PR) Based on Outside Diameter.

ASTM F1962 - Standard Guide for Use of Maxi-Horizontal Directional Drilling for Placement of Polyethylene Pipe or Conduit Under Obstacles, Including River Crossings.

ASTM F2620 - Standard Practice for Heat Fusion Joining of Polyethylene Pipe and Fittings.

AWS A5.8M/A5.8 - Specification for Filler Metals for Brazing and Braze Welding.

AWWA C110/A21.10 - Ductile-Iron and Gray-Iron Fittings.

AWWA C111/A21.11 - Rubber-Gasket Joints for Ductile-Iron Pressure Pipe and Fittings.

AWWA C151/A21.51 - Ductile-Iron Pipe, Centrifugally Cast.

AWWA C153/A21.53 - Ductile-Iron Compact Fittings.

AWWA C509 - Resilient-Seated Gate Valves for Water Supply Service.

AWWA C511 - Reduced-Pressure Principle Backflow Prevention Assembly.

AWWA C515 - Reduced-Wall, Resilient-Seated Gate Valves for Water Supply Service.

AWWA C900 - Polyvinyl Chloride (PVC) Pressure Pipe and Fabricated Fittings, 4 In. through 60 In. (100 mm through 1500 mm).

AWWA C901 - Polyethylene (PE) Pressure Pipe and Tubing, 3/4 In. (19 mm) Through 3 In. (76 mm), for Water Service.

AWWA C906 - Polyethylene (PE) Pressure Pipe and Fittings, 4 In. through 65 In. (100 mm through 1650 mm), for Waterworks.

AWWA M23 - PVC Pipe—Design and Installation.

IAPMO (UPC) - Uniform Plumbing Code.

MSS SP-67 - Butterfly Valves.

MSS SP-80 - Bronze Gate, Globe, Angle, and Check Valves.

MSS SP-110 - Ball Valves Threaded, Socket-Welding, Solder Joint, Grooved and Flared Ends.

ACTION SUBMITTALS

Submit the following per Section << 01 3300 - Submittal Procedures>>:

Catalog data on pipe materials, pipe fittings, valves, and accessories and directional drilling pull (weak link) device and casing seals.

Installation instructions for valves and accessories.

Existing system pressure calculations to support new water pipe design and selection.

Certification of welders and qualified welding procedure.

        - ******************************************************************************

        - The following is a designer choice. If selected, it will activate HDD information in PART 3.

        - ******************************************************************************

Submittals for the Horizontal Direction Drilling.

Tracing wire continuity test report.

Catalog data on identification tape and tracing wire.

LANL-PERFORMED WORK

LANL Utilities and Infrastructure (UI) group will perform final tie-in into existing water piping systems using Subcontractor-supplied material.

LANL FURNISHED AND INSTALLED EQUIPMENT

LANL will furnish and install post indicator valve padlocks.

QUALITY ASSURANCE

Welders Certifications, Qualified Procedure Standards, and Weld Inspection/Testing.

Plastic Pipe: Comply with LANL ESM Chapter 13 – Welding, Joining & NDE.

On-site and joining welding shall comply with LANL ESM Chapter 13 – Welding, Joining & NDE; and Section ​<< 01 4455 - Onsite Welding, Brazing and Joining Requirements>>​.

Use LANL Welding Procedures.

Welders shall be qualified at LANL by LANL.

Off-site welding and joining shall comply with LANL ESM, Chapter 13 – Welding, Joining & NDE; and Section << 01 4444 - Offsite Welding, Brazing and Joining Requirements>>.

Weld Inspection: Comply with LANL ESM Chapter 13 – Welding, Joining & NDE for PE pipe.

LANL Subcontract Technical Representative (STR) shall submit the approved material and accessory catalog data, and certification of welders and qualified welding procedure to the LANL UI Water System Engineer and the LANL Construction Inspector for verification of construction items and certifications during field quality assurance.

PART 2 - PRODUCTS

PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section ​<< 01 2500 - Substitution Procedures>>​.

      - ***************************************************************************************

      - Consult with the LANL UI water system representative for approval when selecting buried piping beyond the building wall and under roads. Provide permanent buildings with a minimum pipe size of 4 inches for potable water supply line.

      - AWWA C151 Available Pipe Size: 4-64 inches.

      - Designer shall account for the diminished interior diameter of polyethylene pipe when designing for facility volume and velocity requirements.

      - The following twelve PART 2 Articles are designer choices based on project-specific requirements. Within each Article, paragraphs related to pipe material types, fitting types, component size ranges, etc. are designer choices based on project-specific requirements.

      - ***************************************************************************************

Water distribution piping BEyond building wall

Ductile Iron Pipe: <<AWWA C151/A21.51>>.

Joints: Bell and spigot, <<AWWA C111/A21.11>> rubber gaskets.

Fittings: <<AWWA C110/A21.10>>, Ductile-Iron or Gray-Iron, Class 350 or <<AWWA C153/A21.53>>​, Ductile-Iron Compact Fittings, Class 350.

Pipe and Fittings: Cement mortar lined with bituminous outside coating.

Copper Tubing: <<ASTM B88>>, Type K, hard drawn or annealed.

Joints: <<AWS A5.8M/A5.8>>, BCuP silver braze.

Fittings: <<ASME B16.22>>​, wrought copper and copper alloy solder-joint.

      - ***************************************************************************************

      - For PVC, AWWA C900 available pipe size is 4-12 inches.  Use ductile iron if static pressure is greater than 200 psig; system is dedicated, pumped fire protection pipeline; or pipeline is routed too close to an active steam line.  See minimum utility line clearances in LANL ESM Chapter 3 - Civil.

      - ***************************************************************************************

PVC Pipe: <<AWWA C900>>​, DR18, pressure class 235.

Joints: Bell and spigot joint <<ASTM D3139>> rubber gaskets <<ASTM F477>>​.

Fittings: <<AWWA C110/A21.10>>, Ductile-Iron or Gray-Iron, Class 350 or <<AWWA C153/A21.53>>, Ductile-Iron Compact Fittings, Class 350.

Polyethylene Pipe and Fittings: <<AWWA C901>> and <<ASTM D3035>> (3 inch or less) and <<AWWA C906>> and <<ASTM F714>> (4 inch to 63 inch), ​<< Class 150, pressure rating 150; or  Class 200, pressure rating 200>>​.

Manufacturer: Performance Pipe – DriscoPlex 4000 FM, Ductile Iron Pipe Size (or as approved by LANL UI Water System Engineer).

Pipe: Polyethylene, high density, <<AWWA C901>>, <<AWWA C906>>, PPI-PE 4710, <<ASTM D3350>> cell classification number PE 445574C.  Certifications by Factory Mutual Approvals Standard (FMA) Class Number 1613 and National Sanitation Foundation (NSF).

Fittings: Polyethylene, high density, <<AWWA C901>>, <<AWWA C906>>, <<ASTM D3261>>, PPI-PE 4710, <<ASTM D3350>> cell classification number PE 445574C.  Certifications by Factory Mutual Approvals (FMA) and National Sanitation Foundation (NSF) NSF/ANSI 61.  The pipe manufacturer shall supply fittings and adapters.

Joints: Heat fusion per <<ASTM F2620>> and manufacturer’s written instruction.

FLANGES, UNIONS, AND COUPLINGS

Copper Tubing:

Class 150 bronze unions with soldered joints.

Mechanical or Push-On Type Pipe, and Fittings Below Grade.

UL listed or FM approved.

Ductile Iron Pipe: Megalug Series 1100, malleable/ductile iron joint retainer/restraint gland with polymer, epoxy or bituminous outside coating and 1/2 inch minimum diameter asphalt coated tie rods.

Ducture Iron Pipe: Tyler Union, American Cast Iron Pipe Company, Star Pipe Products, solid sleeves, long style, MJ x MJ with appropriate sized gasket material. <<AWWA C153/A21.53>>​, Class 350. Steel, size suitable for pipeline material and diameter.

PVC Pipe: for ductile iron joint use a compression connection and restraint system or retainer/restraint gland, Mueller AquaGrip System, Megalug Series 2000PV.

HDPE Pipe: for ductile iron joint use restraint devices designed to resist pull out forces. Internal pipe wall stiffeners must be used when restraining HDPE. Megalug Series 2000PV.

High Density Polyethylene

Flanges: Flanged joints shall be standard manufacturers flange adaptor that is butt fused to the pipe. Backup ring shall be ductile iron. Flange gaskets shall be installed.

Transitions: MJ Adaptors shall be standard manufacturers adaptor that is butt fused to the pipe for connecting to mechanical joint pipe, fittings, and appurtenances.  Manufacturers’ complete assembly shall be supplied; including stainless steel stiffener, extended gland bolts and nuts, gland and gasket.

VALVES, ABOVE GRADE

Ball Valves up to 2 inches:

Manufacturer: Nibco, Series 585-70.

<<MSS SP-110>>, 600 psi CWP, bronze, two piece body, chrome plated brass ball, full port, teflon seats and stuffing box ring, blowout proof stem, lever handle, solder or threaded ends.

Butterfly Valves over 2 inches:

Manufacturer: Nibco, Series LD 2000.

<<MSS SP-67>>, 200 psi CWP, ductile iron body, aluminum bronze disc, resilient replaceable EPDM seat, lug style, extended neck, lever handle, for use between ANSI Class 125/150 flanges.

Globe Valves up to 2 inches:

Manufacturer: Nibco, Series 211.

<<MSS SP-80>>, Class 125 bronze body, bronze trim, hand wheel, bronze disc, solder or threaded ends.

Gate Valves up to 2 inches:

Manufacturer: Nibco, Series 111.

<<MSS SP-80>>, Class 125 bronze body, bronze trim, rising stem, hand wheel, inside screw, solid wedge disc, solders or threaded ends.

VALVES, BELOW GRADE

      - ***************************************************************************************

      - Comply with LANL Civil Standard Details, ST-G3010-2 and ST-G3010-3 for below grade shut-off valve piping details.

      - ***************************************************************************************

Gate Valves less than 2 inches:

Manufacturer: Nibco, Series T-176-A.

<<MSS SP-80>>, Class 300 bronze body, bronze trim, non-rising stem, hand wheel, inside screw, solid wedge disc, threaded ends.

Gate Valves 2 inches and over:

Manufacturer: Mueller, No. A-2362-8, 2 through 3 inch threaded, 2-inch-square wrench nut or No. A-2361-20 with accessories, use No. A-2361-23 when using retainer/restraint gland, or A-2361-77 AquaGrip System for PVC pipe, 4 inch and larger, 2-inch-square wrench nut.

<<AWWA C509>> for 2 and 3 inch, <<AWWA C515>> for 4 through 12 inch, 250 psig and 350 psig pressure, UL-listed or FM-approved, non-rising stem, open left, threaded inlet and threaded outlet or mechanical joint inlet and outlet with mechanical joint with accessories unassembled, less accessories, or with appropriate transition gasket.

Tapping Valves 2 inches and over:

Manufacturer: Mueller, No. T-2360-16 with accessories, use No. T-2360-19 when using retainer/restraint gland, 2 through 3 inch, 2 inch square wrench nut or Mueller, No. T-2361-16 with accessories, use No. T-2361-19 when using retainer/restraint gland, 4 inch and larger.  No substitution.

<<AWWA C509>> for 2 and 3 inch, <<AWWA C515>> for 4 through 12 inch, 250 psig and 350 psig pressure, UL listed or FM approved, resilient wedge, non-rising stem, open left, ANSI Class 125/150 inlet flange, mechanical joint outlet with mechanical joint with accessories or less accessories, 2 inch square wrench nut.

Gate Valve (Post Indicator):

Manufacturer: Mueller, No. P-2361-20, with accessories, use No. P-2361-23 when using retainer/restraint gland, No Substitution.

UL listed and FM approved, 350 psig, non-rising stem with post indicator flange, open left, mechanical joint inlet and outlet with mechanical joint with accessories or less accessories.

WATER PRESSURE REDUCING VALVEs (PRV)

      - ***************************************************************************************

      - Install PRV(s) in appropriately sized concrete vaults allowing full access for maintenance. A LANL UI water system representative shall approve design and installation of site PRVs and required PRV optional features. Comply with LANL ESM Chapter 6 - Mechanical for building PRVs.

      - ***************************************************************************************

​Ductile Iron Body

Manufacturers:

CLA-VAL, No. 90-01, No Substitution.

CLA-VAL, No. 90-48, Low Flow Bypass, No Substitution.

Description:

Single seated, hydraulically operated, pilot controlled, diaphragm type valve, 175 psi pressure rating, 180 degree F maximum water temperature and 15 to 75 psi adjustment range. Pilot control; direct acting, adjustable, spring loaded, and normally open. Valve construction; globe, ductile iron main valve body and cover, bronze main valve trim, and cast bronze pilot control with stainless steel trim. Repairs must be done without removing valve from line.

Optional Features: ​<< CV Flow Control (opening);  CV Speed Control (closing);  CK2 Isolation Valve; and  _______>>​

Capacity/Size/End Connections:

Flow: << _______>>​​ gpm

Size: << ______>> inches

End Connections: NPT ends or <<ASME B16.42>> ANSI Class 150 flanged ends.

Include NPT unions when purchasing with NPT end connections.

Bronze Body

Manufacturers:

CLA-VAL, No. 990, No Substitution.

Watts Regulator Company, No. 25AUB or No. U5B, No Substitution.

Description:

Balanced single seat with bronze valve body and cover, stainless steel trim, integral strainer, 175 psi maximum water pressure, and standard adjustment range 8-80 psi. Repairs must be done without removing valve from line.

Capacity/Size/End Co:

Flow: ​<< _______>>​ gpm

Size: << _______>>  inches

End Connections: NPT union ends.

FIRE HYDRANTS

      - ***************************************************************************************

      - Comply with LANL Civil Standard Detail ST-G3010-4 for fire hydrant piping detail.

      - ***************************************************************************************

Manufacturer: Mueller, Super Centurion 250, Style A423.  No Substitution.

UL listed or FM approved, dry barrel, 5 1/4 inch main valve opening, 3-way with 4 1/2 inch pumper nozzle and two 2 1/2 inch hose nozzles, ground level break flange, and mechanical joint inlet connection or Mueller AquaGrip System.  Hydrant factory painted yellow.

POST INDICATORS

      - ***************************************************************************************

      - Comply with LANL Civil Standard Detail ST-G3010-3 for PIV piping detail.

      - ***************************************************************************************

Manufacturer: Mueller, No. A20806.  No Substitution.

UL listed or FM approved, adjustable type, open left, complete with lower barrel sized for appropriate bury depth.

      - ***************************************************************************************

      - A LANL UI water system representative shall approve design and installation of backflow preventers installed outside the building. Do not install backflow preventer below grade.

      - ***************************************************************************************

BACKFLOW PREVENTER

Threaded Ends (Sizes up to 2 inches)

Manufacturer: Watts Regulator Series 909 or models listed in the latest edition of Approved Backflow Prevention Assemblies by the University of Southern California Foundation for Cross Connection Control and Hydraulic Research.

Assembly, reduced-pressure, bronze body, with ball-type shut-off valves, FNPT ends, test cocks for in-line field testing, integral unions between body and shut-off valves, water temperature range 33 to 140 degrees F, rated working pressure 175 psi, meeting <<AWWA C511>> and <<ASSE 1013>>.  Provide matching air gap drain.

Size: << _______>> inch.

Flanged Ends (2-1/2 inches and larger)

Manufacturer: Watts Regulator Series 909RPDA or models listed in the latest edition of Approved Backflow Prevention Assemblies by the University of Southern California Foundation for Cross Connection Control and Hydraulic Research.

Assembly, reduced-pressure, ductile or cast iron body epoxy coated internal and external, with UL approved OS & Y resilient wedge gate shut-off valves, flanged ends, test cocks for in-line field testing.  Water temperature range 33 to 140 degrees F, working pressure 175 psi, meeting <<AWWA C511>> and <<ASSE 1013>> and/or <<ASSE 1047>>​.  Provide matching air gap drain.

Size: << _______>> inch.

PRESSURE GAUGE

      - ***************************************************************************************

      - Refer to manufacturer’s recommendation for gauge pressure ranges.  Generally, a pressure range of twice the working pressure is recommended, with maximum working pressure not exceeding 75 percent of the range.  If pulsation occurs, working pressure should not exceed 65 percent of the pressure range.

      - ***************************************************************************************

Manufacturer: Reotemp Instruments.

ANSI/<<ASME B40.100>>, Grade A, 1 percent full scale accuracy, minimum 2 1/2 inch dial, phenolic or steel case, phosphor bronze bourdon tube and 1/4 inch NPT brass bottom connection. Furnish with brass ball valve.

Range: << ____ to ____ psi; or   see Drawings>>.

SERVICE SADDLE

      - ***************************************************************************************

      - A LANL UI water system representative shall approve the design and installation of proposed taps on asbestos-cement water lines. Asbestos-cement lines cannot be tapped directly; portion of main line will be replaced by LANL UI.

      - ***************************************************************************************

Manufacturer: Mueller, DR1A & S Series and DR2A & S Series for A-C and plastic.

Ductile iron, stainless steel strap, iron pipe outlet thread, and o-ring gasket.

Strap shape to be per manufacture recommendation for the existing pipe material.

TAPPING SLEEVE

      - ***************************************************************************************

      - A LANL UI water system representative shall approve the design and installation of proposed taps on asbestos-cement water lines. Asbestos-cement lines cannot be tapped directly; portion of main line will be replaced by LANL UI.

      - ***************************************************************************************

Manufacturer: Romac Industries, No. FTS 419, No Substitution.

Fabricated steel, ANSI Class 150 outlet flange, suitable for PVC, steel, ductile iron, and cast iron pipe, outlet flange size and sleeve O.D. to suit piping system, 4 inch and larger.

VALVE BOX

      - ***************************************************************************************

      - Comply with LANL Civil Standard Detail ST-G3010-1 for valve box detail.

      - ***************************************************************************************

Manufacturer: Tyler, Series 6860.

Cast iron, 5 1/4 inch shaft, screw type, lid marked “water”.

PART 3 - EXECUTION

EXAMINATION

Do not install underground piping when bedding is wet or frozen.

Verify that excavations are to required grade.

PREPARATION

Ream pipe and tube ends.  Remove burrs.

Remove scale and dirt on inside and outside of piping before assembly.

Keep open ends of pipe free from scale and dirt.  Whenever work is suspended during construction, or at the end of each workday, protect open ends with temporary plugs or caps.

PIPING TIE-IN

      - ***************************************************************************************

      - Refer to LANL Civil Standard Detail ST-G3010-2 for water piping tie-in details.

      - ***************************************************************************************

Tie-in to existing piping systems will be performed by LANL UI group. Excavation, backfill, and materials required for tie-in shall be provided by Subcontractor. The tie-in will be inspected by the LANL STR and the LANL UI Water System Representative.

New tie-ins shall be a minimum size of 2 inches when tying into existing piping systems that are 4 inches and larger.  If required, a pipe size reduction shall be made after the valve.

New tie-ins to existing piping systems 4 inches and larger shall be made by using a tee cut into the existing pipe and a valve on the new service line.  If the existing line cannot be removed from service a tapping tee and tapping valve can be used.

LANL STR will notify LANL UI group at least 15 working days in advance to schedule tie-in.

Before tie-ins are scheduled, the LANL STR will ensure materials required for tie-in are on site, service lines have been tested and disinfected, material submittals and all test reports have been approved by LANL UI Group, and bell hole excavation meets access and OSHA requirements.

BURIED PIPING

      - ***************************************************************************************

      - Tracer wire and test stations are required when specifying cast iron, ductile iron, and non-metallic piping. Comply with LANL Civil Standard Details ST-G30GEN-3 for tracer wire/test station details and ST-G30GEN-4 for trenching detail.

      - Refer to the LANL ESM Chapter 3 - Civil, Section G30, for required minimum utility line clearances.

      - Refer to LANL Civil Standard Detail  ST-G30GEN-4 for trench width and piping burial depth.

      - ***************************************************************************************

Refer to Drawings and Section << 31 2000 - Earth Moving>>, for earth cover, bedding, tracer wire, wire continuity test, warning tape, documenting new or exposed existing utility location, etc., requirements.

Minimum cover over pipe shall be 48 inches measured from finish grade to top of pipe.

INSTALLATION

Comply with <<IAPMO (UPC)>> and applicable AWWA publications.

Provide non-conducting dielectric connections wherever jointing dissimilar metals.

Route piping in a straight line, in an orderly manner, and maintain gradient.

      - ***************************************************************************************

      - Retain the following paragraph when fire hydrants are required for project.

      - ***************************************************************************************

Set hydrants plumb and locate pumper nozzle perpendicular to and facing roadway.

Install piping to allow for expansion and contraction without stressing pipe, joints, or connected equipment.

Sleeve and caulk pipes penetrating exterior walls below grade to provide a waterproof installation.

      - ***************************************************************************************

      - Disinfecting solutions containing chlorine shall not exceed 12% active chlorine, greater concentrations can chemically attack and degrade polyethylene.

      - ***************************************************************************************

Disinfect water distribution system per Section << 22 0816 - Disinfection of Potable Water Piping>>​.

Pressure test piping system per Section << 22 0813 - Testing Piping Systems>>.

      - ***************************************************************************************

      - Consult with a LANL Fire Protection Group representative and a LANL UI  water system representative for sites with dedicated non-potable water fire lines.

      - ***************************************************************************************

Fire hydrants tied into a non-potable dedicated fire loop shall have the hydrant bonnet painted black, and labeled “Non-Potable Water, Do Not Drink” per Section << 22 0554 - Identification for Plumbing,  HVAC, and Fire Piping and Equipment>>. Refer to Drawings for hydrant location.

Comply with <<AWWA M23>>, PVC Pipe Design Installation, for installation of PVC piping under roads.

      - ***************************************************************************************

      - Retain the following Article when polyethylene piping is selected for project.

      - ***************************************************************************************

POLYETHYLENE PIPING INSTALLATION

      - ***************************************************************************************

      - Use metallic pipe if water line is installed less than 20 feet from steam and condensate lines.

      - ***************************************************************************************

Lay coiled and small diameter piping on trench bottom in such a manner as to snake piping (“S” curves) in trench along the piping run.  This will insure that sufficient piping material is available for expansion and contraction.  Lay piping in trench and allow for temperature stabilization to minimize thermal expansion and contraction.

Cold (field) bending allowable bend radius is determined by pipe diameter and dimension ratio.  Minimum bend radius shall be per manufacturers written instructions.  Bends shall not be made where fittings are in the bend.

Provide minimum of 5 feet of cover over piping installed under any roadways and vehicle parking areas.

Perform butt heat-fusion joining in accordance with <<ASTM F2620>> and the manufacturer’s written instructions.  See PART 1, Quality Assurance article.

Make connections to PE-to-DI or PVC pipe and mechanical connections, valves, and appurtenances with transition fittings that are butt fused onto the PE pipe. Provide complete assemblies and install per manufacturers written instruction.

Thrust blocks and restraint shall be installed at fire hydrants, tees and change in direction per the manufacturer’s written instructions.

      - ***************************************************************************************

      - Retain the following Article when horizontal directional drilling or pipe bursting required for project.

      - ***************************************************************************************

Horizontal Directional Drilling or Pipe Bursting

Crossing of paved streets or roadways or other areas, if approved by LANL UI Representative, may be accomplished by horizontal directional drilling (HDD) or pipe bursting, whenever practical. The HDD bore shall be kept to a maximum of 2 inches larger than the pipe. Care shall be exercised to ensure the paved surface is not damaged during the drilling operation.

Top of HDD shall have a minimum below grade bury depth of 48 inches and a minimum bury depth of 60 inches below any paved surface. Depth shall not exceed excavation by standard, conventional means and shall be approved by LANL UI Representative.

When pulling in pipe the pulling force shall be monitored and kept below the Allowable Tensile Load (ATL) value of the pipe size and material per manufacturer’s recommendation. Both pipe ends shall be monitored for continuous, smooth movement. Pulling load from the equipment shall be monitored and the pipe lead end shall be equipped with a weak link device to disengage at the ATL or below. Manufacturer’s procedures and design parameters shall be followed, in addition to <<ASTM F1962>>.

Polyethylene pipe shall extend 3-5 percent of the pulled-in length past the termination points to allow for contraction. Polyethylene pipe shall be allowed 24 hours to recover from the pulling stress and contract to original pre-pull length and allowed to stabilize to buried soil temperature before final tie-ins are accomplished. A minimum of five (5) feet of pipe shall extend beyond the drilling entrance/exit hole to allow for pipe damage assessment. Tracing wire shall be pulled in with the polyethylene pipe.

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 33 1000, REV. 10, DATED APRIL 15, 2026.