Section 33 3000 
Sanitary Sewerage Utilities

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION section

Rev. 8 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Civil POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality sections.

  - *************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

      - ***************************************************************************************

      - The following paragraphs are designer choices based on project-specific requirements.

      - ***************************************************************************************

Sanitary Sewer Piping, Buried Beyond 5 Feet of Building

Flanges, Unions, and Couplings (Sewer Force Mains)

Cleanouts

Manhole

related requirements

Section << 01 2500 - Substitution Procedures>>

Section << 01 4444 - Offsite Welding, Brazing and Joining Requirements>>

Section << 01 4455 - Onsite Welding, Brazing and Joining Requirements>>

Section << 03 3053 - Miscellaneous Cast-in-Place Concrete>>​

Section << 22 0813 - Testing Piping Systems>>

Section << 31 2000 - Earth Moving>>​

Section << 33 0513 - Manholes and Structures>>​

REFERENCE STANDARDS

ASTM D3034 - Standard Specification for Type PSM Poly(Vinyl Chloride) (PVC) Sewer Pipe and Fittings.

ASTM D3035 - Standard Specification for Polyethylene (PE) Plastic Pipe (DR-PR) Based on Controlled Outside Diameter.

ASTM D3139 - Standard Specification for Joints for Plastic Pressure Pipes using Flexible Elastomeric Seals.

ASTM D3212 - Standard Specification for Joints for Drain and Sewer Plastic Pipes Using Flexible Elastomeric Seals.

ASTM D3261 - Standard Specification for Butt Heat Fusion Polyethylene (PE) Plastic Fittings for Polyethylene (PE) Plastic Pipe and Tubing.

ASTM D3350 - Standard Specification for Polyethylene Plastics Pipe and Fittings Materials.

ASTM F477 - Standard Specification for Elastomeric Seals (Gaskets) for Joining Plastic Pipe.

ASTM F585 - Standard Guide for Insertion of Flexible Polyethylene Pipe Into Existing Sewers.

ASTM F714 - Standard Specification for Polyethylene (PE) Plastic Pipe (DR-PR) Based on Outside Diameter.

ASTM F1962 - Standard Guide for Use of Maxi-Horizontal Directional Drilling for Placement of Polyethylene Pipe or Conduit Under Obstacles, Including River Crossings.

AWWA C110/A21.10 - Ductile-Iron and Gray-Iron Fittings.

AWWA C111/A21.11 - Rubber-Gasket Joints for Ductile-Iron Pressure Pipe and Fittings.

AWWA C151/A21.51 - Ductile-Iron Pipe, Centrifugally Cast.

AWWA C153/A21.53 - Ductile-Iron Compact Fittings.

AWWA C900 - Polyvinyl Chloride (PVC) Pressure Pipe and Fabricated Fittings, 4 In. through 60 In. (100 mm through 1500 mm).

New Mexico Plumbing Code - New Mexico Plumbing Code.

LANL-PERFORMED WORK

Coordinate with the LANL Subcontractor Technical Representative (STR) for ties into existing systems which include sanitary sewer lines, septic tanks, treatment plants, lift stations, and manholes. Ties into existing systems shall be performed by LANL Utilities and Infrastructure Group (UI).

LANL STR will coordinate for inspection of the interior of new and existing sanitary sewer lines (accessible by camera) with video camera for piping integrity and proper installation both before tie-in and at turnover.

      - ***************************************************************************************

      - Design Agency shall coordinate with LANL Projects Manager to ensure an approved WPF (Waste Profile Form) for all anticipated wastewater flows has been submitted to the LANL WAC Committee and Utility Wastewater system Operations Manager representative prior to completion of design.

      - ***************************************************************************************

LANL STR will ensure that an approved WPF (Waste Profile Form) for all anticipated wastewater from all drains or buildings connected to the sanitary wastewater system has been completed by LANL Project Manager and on file before scheduling tie-ins.  Documentation shall be submitted to the LANL UI Wastewater System Representative prior to utility tie-in.

LANL STR will coordinate all required inspections and tie-ins.

ACTION SUBMITTALS

Catalog data on pipe materials, fittings and accessories, directional drilling pull (weak link) device, and casing seals.

Certifications of welders qualified welding procedure for heat fusion polyethylene joints.

      - ***************************************************************************************

      - The following is a designer choice.

      - ***************************************************************************************

Submittals for the Horizontal Directional Drilling.

Tracing wire continuity test report.

QUALITY ASSURANCE

Welders Certifications, Qualified Procedure Standards, and Weld Inspection/Testing.

Plastic Pipe: Comply with LANL ESM Chapter 13 – Welding, Joining & NDE.

On-site and joining welding shall comply with LANL ESM Chapter 13 – Welding, Joining & NDE; and Section << 01 4455 - Onsite Welding, Brazing and Joining Requirements>>.

Use LANL Welding Procedures

Welders shall be qualified at LANL by LANL

Off-site welding and joining shall comply with LANL ESM Chapter 13 – Welding, Joining & NDE; and Section ​<< 01 4444 - Offsite Welding, Brazing and Joining Requirements>>​.

Weld Inspection: Comply with LANL ESM Chapter 13 – Welding, Joining & NDE for polyethylene pipe.

LANL STR shall submit the approved material and accessory catalog data, and certification of welders and qualified welding procedure to the LANL UI Wastewater System Engineer and the LANL Construction Inspector for verification of construction items and certifications during field quality assurance.

PART 2 - PRODUCTS

PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section << 01 2500 - Substitution Procedures>>​.

      - ***************************************************************************************

      - The following four Articles are designer choices based on project-specific requirements. Within each Article, paragraphs related to pipe material types, fitting types, component size ranges, etc. are designer choices based on project-specific requirements.

      - ***************************************************************************************

SANITARY SEWER PIPING, BURIED BEYOND 5 FEET OF BUILDING

      - ***************************************************************************************

      - Consult with a LANL UI Wastewater System Representative for approval when selecting piping material beyond 5 feet of the building and under roads. Under roadways will require ductile iron or metallic pipe sleeve with spacers. Sanitary sewer force main fittings shall have thrust blocks and restraints.

      - ***************************************************************************************

Ductile Iron Pipe: <<AWWA C151/A21.51>>, Class 150.

Joints: Bell and spigot, <<AWWA C111/A21.11>>​ rubber gaskets.

Fittings: <<AWWA C110/A21.10>>,, Class 350 or <<AWWA C153/A21.53>>​, Class 350.

PVC Pipe and Fittings: <<ASTM D3034>>, SDR 35.

Joints: Bell and spigot, <<ASTM D3212>> rubber gaskets.

      - ***************************************************************************************

      - Specify the following paragraphs for pressure systems (non-gravity)

      - ***************************************************************************************

PVC Pipe: <<AWWA C900>>, Class 150 (DR 18).

Joints: Bell and spigot joint <<ASTM D3139>>, rubber gaskets <<ASTM F477>>.

Fittings: <<AWWA C110/A21.10>>, Class 350 or <<AWWA C153/A21.53>>, Class 350.

Ductile Iron Pipe: <<AWWA C151/A21.51>>​, Class 150.

Joints: Bell and spigot, <<AWWA C111/A21.11>>​ rubber gaskets.

Fittings: <<AWWA C110/A21.10>>, Class 350 or <<AWWA C153/A21.53>>, Class 350.

      - ***************************************************************************************

      - Polyethylene Pipe may be used for gravity and pressure systems. The SDR pipe shall be sized to meet design pressure rating requirements of lift station pumps.

      - ***************************************************************************************

Polyethylene Pipe and Fittings.

Manufacturer: Performance Pipe, ​​<< DriscoPlex 4100, Iron Pipe Size (IPS); or  DriscoPlex 4000, Ductile Iron Pipe  Size (DIPS)>>​​. Use of IPS or DIPS shall be appropriate for new system or interface with existing system.

Pipe: Polyethylene, high density, <<ASTM D3035>>, <<ASTM F714>>, PE4710, << SDR 11; or  _______>> pipe size, <<ASTM D3350>> cell classification number 445574C.

Fittings: Polyethylene, high density, butt heat fusion type, <<ASTM D3261>>, PE4710, ​<< SDR 11; or  _______>>​, <<ASTM D3350>> cell classification number 445574C.

Joints: Heat fusion per manufacturer’s instruction.

FLANGES, UNIONS, AND COUPLINGS (Sewer Force Mains)

Mechanical or Push-On Type Pipe, and Fittings Below Grade.

Ductile Iron Pipe: Megalug Series 1100, malleable/ductile iron joint retainer/restraint gland with polymer, epoxy or bituminous outside coating and 1/2 inch minimum diameter asphalt coated tie rods.

PVC Pipe: Use a compression connection and restraint system or retainer/restraint gland, Megalug Series 2000PV.

High Density Polyethylene

Transitions: MJ Adaptors shall be standard manufacturers adaptor that is butt fused to the pipe for connecting to mechanical joint pipe, fittings, and appurtenances.  Manufacturers’ complete assembly shall be supplied; including stainless steel stiffener, extended gland bolts and nuts, gland and gasket.

Coupling Sleeve Gravity Pipe

Manufacturer: Fernco Flexible Coupling or Proflex Coupling for heavy earth loadings.  Gasket suitable for the pipe material being joined.

Coupling Sleeve Pressure Pipe

Manufacturer: Tyler Union, American Cast Iron Pipe Company, Star Pipe Products, solid sleeves, long style, MJ x MJ with appropriate sized gasket material.  <<AWWA C153/A21.53>>, Class 350.

CLEANOUTS

Cleanout

Manufacturer:  General Engineering Company, GENECO.

Ferrous metal top with gasketed bell to accept PVC schedule 40 or cast iron riser pipe.

Screw plug to be standard brass countersunk plug.

Riser Pipe

Pipe: 4 inch minimum PVC schedule 40 or heavier or cast iron.

Wye

Preformed single wye or double wye per design requirement.

MANHOLE

      - *********************************************************************************

      - Refer to LANL Civil Standard Detail ST-G3020-1 for manhole detail.

      - ***************************************************************************************

Provide precast concrete manhole, concrete grade rings, and ductile iron cover per Drawings and Section << 33 0513 - Manholes and Structures>>.

PART 3 - EXECUTION

EXAMINATION

Verify excavations are to required grade.  Do not over excavate.

PREPARATION

Ream pipe ends and remove burrs.

Remove scale and dirt on inside and outside of piping before assembly.  Pipe interior shall be thoroughly cleaned of foreign material before lowering into the trench.

Keep open ends of pipe free from scale and dirt.  Whenever work is suspended during construction, or at the end of each workday, protect open ends with temporary plugs or caps.

PIPING TIE-IN

Tie-ins to existing piping, lift stations, manholes, and equipment will be performed by LANL UI group. Excavation, backfill, and materials required for tie-in shall be provided by Subcontractor. The tie-in will be inspected by the LANL Construction Inspector and the LANL UI Wastewater Systems Representative.

LANL STR will notify LANL UI at least 15 working days in advance to schedule tie-in of piping system and pre-tie-in video inspection described in Article << 3.7; or  _______>>LANL Acceptance Inspection and Testing.

Before tie-ins are scheduled the LANL STR will ensure materials required for tie-in are on site, service lines have been tested, material submittals and all test reports have been approved by LANL UI and the excavation meets access and OSHA requirements.

Install pipe at manhole tie-ins at the same invert elevation without sags or low points.  Chip manhole wall only to allow for insertion of new pipe.  Install waterstop grout ring around the pipe before repairing the manhole wall. Caulk/seal around new pipe to provide watertight installation in manhole wall.  Seal shall be per pipe manufacturer’s instructions, in addition to <<ASTM F585>>.

Sleeve and caulk pipes penetrating exterior walls below grade to provide a waterproof installation.

Set concrete manholes level and plumb and test manholes for leakage per Section << 33 0513 - Manholes and Structures>>.

BURIED PIPING

      - ***************************************************************************************

      - Tracer wire and test stations are required when specifying cast iron, ductile iron, and non-metallic piping.  Comply with LANL Civil Standard Detail ST-G30GEN-3 for tracer wire/test station details and LANL Civil Standard Detail ST-G30GEN-4 for trenching detail.

      - Refer to the LANL ESM Chapter 3 - Civil, Section G30 for required minimum utility line clearances.

      - Use metallic pipe if PVC or PE sewer line pipe is installed less than 20 feet from steam and condensate lines.

      - ***************************************************************************************

Refer to Drawings and Section << 31 2000 - Earth Moving>>​ for cover, bedding, tracer wire, wire continuity test, warning tape, documenting new or exposed existing utility location, and other requirements.

Slope of service lateral from building to main shall be continuous and uniform without fittings or angled pipe joints.  Slope shall be a minimum slope of 1/4 inch per foot and a maximum slope of 1/2 inch per foot.  Minimum depth of cover shall be 4 feet.

Comply with <<New Mexico Plumbing Code>> (IAPMO UPC and amendments).

Route piping in orderly manner and maintain gradient.

Install bell and spigot pipe with bell end upstream.

Thrust blocks and restraint shall be installed on sanitary sewer force mains at tees, elbows, and change in direction, per the manufacturer’s written instructions and Section << 03 3053 - Miscellaneous Cast-in-Place Concrete>>.

Pressure test piping system with water or air in accordance with Section << 22 0813 - Testing Piping Systems>>.

Minimum cover over pipe shall be 48 inches measured from finish grade to top of pipe.

      - ***************************************************************************************

      - The following Article is a designer choice.

      - ***************************************************************************************

SEWER CLEANOUT

Cleanouts shall consist of single or double preformed wye, riser pipe, and access top.

Double cleanout shall be placed at five feet from building wall. A cleanout shall be placed at a change in direction in service laterals.  The distance between cleanouts in service laterals shall not exceed 100 feet.

Riser pipes shall be one piece extended to grade with top adapter for a countersunk threaded plug.

Sand bedding or fine graded backfill material shall be compacted around riser pipe.

Cleanouts at grade shall have concrete collars eighteen (18) square by six (6) inches thick with 6X6X10 gauge (W1.4) wire fabric reinforcement.  Concrete shall be continuous at double cleanouts.  Collar shall be flush with finish grade or pavement.

      - ***************************************************************************************

      - Retain the following Article when horizontal directional drilling or pipe bursting required for project.

      - ***************************************************************************************

HORIZONTAL DIRECTIONAL DRILLING OR PIPE BURSTING

Crossing of paved streets or roadways or other areas, if approved by LANL UI Representative, may be accomplished by horizontal directional drilling (HDD) or pipe bursting, whenever practical.  The HDD bore backreamer diameter shall be kept to a minimum to allow the pipe to be drawn in.  For HDD the minimum slope for gravity sanitary sewer systems shall be three percent.  Care shall be exercised to ensure the paved surface and other utilities are not damaged during the drilling operation.

Top of HDD shall have a minimum below grade bury depth of 48 inches and a minimum bury depth of 60 inches below any paved surface.  Depth shall not exceed excavation by standard, conventional means and shall be approved by LANL UI Representative.

When pulling in pipe the pulling force shall be monitored and kept below the Allowable Tensile Load (ATL) value of the pipe size and material per manufacturers’ recommendation.  Both pipe ends shall be monitored for continuous, smooth movement.  Pulling load from the equipment shall be monitored and the pipe lead end shall be equipped with a weak link device to disengage at the ATL or below.  Manufacturer’s procedures and design parameters shall be followed, in addition to <<ASTM F1962>>​.

Polyethylene pipe shall extend 3-5 percent of the pulled-in length past the termination points to allow for contraction.  Polyethylene pipe shall be allowed 24 hours to recover from the pulling stress and contract to original pre-pull length and allowed to stabilize to buried soil temperature before final tie-ins are accomplished.  A minimum of five (5) feet of pipe shall extend beyond the drilling entrance/exit hole to allow for pipe damage assessment. Tracing wire shall be pulled in with the polyethylene pipe.

LANL ACCEPTANCE INSPECTION AND TESTING

Notify LANL STR at least 15 working days before tie-in to schedule video inspection of piping system.  Inspection will verify that new and existing lines are clean and acceptable for tie-in to commence.

Notify LANL STR at least 7 working days before system turnover to schedule second and final video inspection of piping system.  The re-inspection is to assure no debris from construction activity has entered the new or existing system.

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING statement IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 33 3000, REV. 8, DATED APRIL 15, 2026.