Section 33 4000 
Storm Drainage Utilities

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 5 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Civil POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable sections from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality sections.

  - *************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

Site storm drainage piping, fittings, and accessories beyond building wall.

        - ******************************************************************************

        - The following subparagraphs are designer choices based on project-specific requirements.

        - ******************************************************************************

Storm Drainage Piping

Corrugated Metal Pipe

Corrugated Polyethylene Pipe and Fittings

Cleanouts

Manholes

Related requirements

Section << 01 2500 - Substitution Procedures>>

Section << 01 4444 - Offsite Welding, Brazing and Joining Requirements>>​

Section << 01 4455 - Onsite Welding, Brazing and Joining Requirements>>

Section << 22 0813 - Testing Piping Systems>>

Section << 31 2000 - Earth Moving>>​

REFERENCE STANDARDS

AASHTO M 36 - Standard Specification for Corrugated Steel Pipe, Metallic-Coated, for Sewers and Drains.

AASHTO M 246 - Standard Specification for Steel Sheet, Metallic-Coated and Polymer-Precoated, for Corrugated Steel Pipe.

AASHTO M 252 - Standard Specification for Corrugated Polyethylene Pipe, 75- to 250-mm (3- to 10-in.) Diameter.

AASHTO M 294 - Standard Specification for Corrugated Polyethylene Pipe, 300- to 1500-mm (12- to 60-in.) Diameter.

AASHTO M 304 - Standard Specification for Poly(Vinyl Chloride) (PVC) Profile Wall Drain Pipe and Fittings Based on Controlled Inside Diameter.

AASHTO M-218 - Standard Specification for Steel Sheet, Zinc-Coated (Galvanized), for Corrugated Steel Pipe.

ASTM A742 - Standard Specification for Steel Sheet, Metallic Coated and Polymer Precoated for Corrugated Steel Pipe.

ASTM A760 - Standard Specification for Corrugated Steel Pipe, Metallic-Coated for Sewers and Drains.

ASTM A929/A929M - Standard Specification for Steel Sheet, Metallic-Coated by the Hot-Dip Process for Corrugated Steel Pipe.

ASTM D1056 - Standard Specification for Flexible Cellular Materials—Sponge or Expanded Rubber.

ASTM D1784 - Standard Classification System and Basis for Specification for Rigid Poly(Vinyl Chloride) (PVC) Compounds and Chlorinated Poly(Vinyl Chloride) (CPVC) Compounds.

ASTM D2321 - Standard Practice for Underground Installation of Thermoplastic Pipe for Sewers and Other Gravity-Flow Applications.

ASTM D3035 - Standard Specification for Polyethylene (PE) Plastic Pipe (DR-PR) Based on Controlled Outside Diameter.

ASTM D3212 - Standard Specification for Joints for Drain and Sewer Plastic Pipes Using Flexible Elastomeric Seals.

ASTM D3261 - Standard Specification for Butt Heat Fusion Polyethylene (PE) Plastic Fittings for Polyethylene (PE) Plastic Pipe and Tubing.

ASTM F405 - Standard Specification for Corrugated Polyethylene (PE) Pipe and Fittings.

ASTM F667/F667M - Standard Specification for 3 through 24 in. Corrugated Polyethylene Pipe and Fittings.

ASTM F714 - Standard Specification for Polyethylene (PE) Plastic Pipe (DR-PR) Based on Outside Diameter.

AWWA C110/A21.10 - Ductile-Iron and Gray-Iron Fittings.

AWWA C111/A21.11 - Rubber-Gasket Joints for Ductile-Iron Pressure Pipe and Fittings.

AWWA C151/A21.51 - Ductile-Iron Pipe, Centrifugally Cast.

AWWA C153/A21.53 - Ductile-Iron Compact Fittings.

PPI - PE4710 - IPS and Large Diameter Metric HDPE Pipe Size Chart.

LANL PERFORMED WORK

LANL Utilities and Infrastructure (UI) will inspect interior of storm drainage lines beyond the building wall with video camera for piping integrity and proper construction.

ACTION SUBMITTALS

Submit the following:

Catalog data on pipe materials, fittings and accessories.

Installation instructions for accessories.

        - ******************************************************************************

        - The following is a designer choice.

        - ******************************************************************************

Certifications of welders qualified welding procedure for heat fusion polyethylene pipe joints.

QUALITY ASSURANCE

Welders Certifications, Qualified Procedure Standards, and Weld Inspection/Testing.

Plastic Pipe:  Comply with LANL ESM Chapter 13 – Welding, Joining & NDE.

On-site and joining welding shall also follow Section << 01 4455 - Onsite Welding, Brazing and Joining Requirements>>.

Use LANL Welding Procedures

Welders shall be qualified at LANL by LANL

Off-site welding and joining shall also follow Section << 01 4444 - Offsite Welding, Brazing and Joining Requirements>>.

Weld Inspection: Comply with LANL ESM Chapter 13 – Welding, Joining & NDE for polyethylene pipe.

LANL Subcontract Technical Representative (STR) shall submit the approved material and accessory catalog data, and certification of welders and qualified welding procedure to the LANL UI Wastewater System Engineer and the LANL Construction Inspector for verification of construction items and certifications during field quality assurance.

PART 2 - PRODUCTS

Product Options and Substitutions

Alternate products may be accepted; follow Section ​<< 01 2500 - Substitution Procedures>>​.

      - ***************************************************************************************

      - The following five Articles are designer choices based on project-specific requirements.

      - ***************************************************************************************

STORM DRAINAGE PIPING

      - ***************************************************************************************

      - Consult with a LANL UI storm water system representative for approval when selecting buried piping material.

      - ***************************************************************************************

Ductile Iron Pipe: <<AWWA C151/A21.51>>.

Joints: Bell and spigot, <<AWWA C111/A21.11>> rubber gaskets.

Fittings: <<AWWA C110/A21.10>>, Ductile-Iron or Gray-Iron, Class 350 or <<AWWA C153/A21.53>>​, Ductile-Iron Compact Fittings, Class 350.

PVC Pipe and Fittings: <<AASHTO M 304>>​ and <<ASTM D1784>>.

Joints: Bell and spigot, <<ASTM D3212>>, rubber gaskets.

Polyethylene Pipe and Fittings.

Manufacturer: Performance Pipe, << DriscoPlex 4100, Iron Pipe Size;  DriscoPlex 4000, Ductile Iron Pipe Size; or  _______>>.  Use of IPS or DIPS shall be appropriate for new system or interface with existing system.

Pipe: Polyethylene, high density, <<ASTM D3035>>, <<ASTM F714>>, <<PPI - PE4710>>, ​<< SDR 11; or  _______>>​ pipe size, <<ASTM D3035>> cell classification number 445574C.

Fittings: Polyethylene, high density, butt heat fusion type, <<ASTM D3261>>, <<PPI - PE4710>>, ​<< SDR 11; or  _______>>​, <<ASTM D3035>> cell classification number 445574C.

Joints:  Heat fusion per manufacturer’s instructions.

CORRUGATED METAL PIPE

Material: Steel base metal with 2 oz. per square foot zinc coating per <<AASHTO M-218>> and <<ASTM A929/A929M>> or polymeric coating <<AASHTO M 246>> and <<ASTM A742>>.

Fabrication: Fabrication by corrugating continuous coils into helical form with lock-seam or by rolling annular corrugated mill sheet per <<AASHTO M 36>> and <<ASTM A760>>; polymeric pipe per <<ASTM A742>>​​ .

Gaskets and Sealants: <<ASTM D1056>> sponge neoprene sleeve gaskets and mastic sealant.

Corrugated polyethylene pipe and fittings

Material: High density polyethylene, <<ASTM F405>> and <<AASHTO M 252>> pipe and  fittings size small, <<ASTM F667/F667M>> and <<AASHTO M 252>> pipe and fitting size medium,  and <<AASHTO M 294>> pipe and fitting size large, 12 inch and larger. Pipe shall have corrugated exterior with smooth interior.

Gaskets and Sealants: <<ASTM D3212>>, flexible elastomeric seals.

Installation: Per manufactures requirements and recommendations of <<ASTM D2321>>​.

CLEANOUTS

Manufacturer: J.R. Smith Mfg. Co.

<< Select cleanouts to suit project.  Refer to manufacturer’s catalog data for selection criteria.>>

MANHOLES

      - ***************************************************************************************

      - Refer to the LANL Civil Standard Details ST-G3030-1 and ST-G3030-2 for catch basin details, and STG3030-3 for manhole detail.

      - ***************************************************************************************

Provide concrete catch basins and pre-cast concrete manhole per details shown on the Drawings.

PART 3 - EXECUTION

exaMINATION

Verify excavations are to required grade.  Do not over excavate.

PREPARATION

Ream pipe ends, remove burrs, and regalvanize damaged surfaces.

BURIED PIPING

      - ***************************************************************************************

      - Tracer wire and test stations are required when specifying ductile iron, and non-metallic piping. Comply with LANL Civil Standard Details ST-G30GEN-3 for tracer wire/test station details and Civil Standard Drawing ST-G30GEN-4 for trenching detail.

      - Refer to the LANL ESM Chapter 3 - Civil, Section G30 for required minimum utility line clearances.

      - ***************************************************************************************

Refer to Drawings and Section << 31 2000 - Earth Moving>>, for earth cover, bedding, tracer wire, wire continuity test, warning tape, documenting new or exposed existing utility location, etc requirements.

Bedding material for corrugated metal pipes shall confirm to Drawings and Section << 31 2000 - Earth Moving>>. Place bedding material under the pipe and around a minimum of 1/3 the diameter of the pipe. Place bedding material to provide uniform   support for the entire length of pipe.

Backfill material for corrugated metal pipes shall consist of a well graded mixture of stone fragments, gravel, and sand. Backfill material shall have a maximum particle size less than 1.5 inches and be free of organic material, frozen clump, or stones.

INSTALLATION

Encase exterior cleanouts in concrete, flush with gradient as shown on drawings.

Route piping in orderly manner and maintain gradient as shown on drawings.

Install bell and spigot pipe with bell end upstream.

Sleeve and caulk pipes penetrating exterior walls below grade to provide a waterproof installation, “excluding corrugated type pipes.”

Pressure test piping system with water in accordance with Section << 22 0813>> excluding corrugated-type pipes.

LANL ACCEPTANCE INSPECTION AND TESTING

LANL Subcontract Technical Representative (STR) will notify LANL UI group at least 15 working days in advance to schedule inspection of piping system and to schedule tie-in.

Before tie-ins are scheduled the LANL STR will ensure materials required for tie-in are on site, service lines have been tested, material submittals and all test reports have been approved by LANL UI Group.

LANL STR will contact LANL UI Group to arrange for video inspection of interior of piping system beyond building wall.  LANL UI Group will perform inspection.

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 33 4000, REV. 5, DATED APRIL 15, 2026.