Section 33 5100 
Natural Gas Distribution

  - ************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 12 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Civil POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable sections from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality sections.

      - ==========================================================

      - The designer is cautioned that the piping design of the distribution system to the exit of the service meter assembly (or, where no meter is provided, the outlet of the service regulator or service shutoff valve) is governed by ASME B31.8 AND 49 CFR 192. The most stringent code or CFR shall apply. While ASME codes are issued at discrete intervals, the CFR may change at any time. The designer should check the CFR website for the most current requirements.

      - After the service point (above), the governing code is NFPA 54, National Fuel Gas Code (replacing ASME B31.2, ANSI Z21.3, and ANSI Z83.1) and should follow Section ​​​<< 23 1123 - Facility Natural-Gas Piping>>​​​.  Other codes may apply for safety features of the gas train.  See LANL ESM Chapter 17 - Pressure Safety for information on those requirements.

  - ************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

Site distribution gas piping system including above and below grade piping and appurtenances upstream of and including the low pressure regulator station.

        - ******************************************************************************

        - The following subparagraphs are designer choices based on project-specific requirements.

        - ******************************************************************************

Polyethylene Piping, Below Grade

Steel Piping, Below Grade

Steel Piping, Above Grade

Pressure Regulator Station

Shut-Off Valve, Above Grade, Threaded Ends, 1 & 2 Inch

Shut-Off Valve, Above Grade, Flanged Ends, 3 Through 12 Inch

Shut-Off Valve, Above and Below Grade, Welded Ends

Shut-Off Valve, Below Grade, Polyethylene

Anodeless Riser

Transition Fitting

Branch Connection

Valve Box

Test Lead Stations

Test Plug (Pete's Plug II or Equal)

Carrier Pipe Spacers and Seal

Related Requirements

Section << 01 2500 - Substitution Procedures>>

Section << 01 3300 - Submittal Procedures>>

Section ​<< 01 4115 - Pressure Safety Submittals>>​

Section << 01 4444 - Offsite Welding, Brazing and Joining Requirements>>

Section << 01 4455 - Onsite Welding, Brazing and Joining Requirements>>

Section << 01 4631 - Welding, Brazing, and Soldering of Pressure Systems>>

Section << 01 4731 - Flange Assembly for Pressure Systems>>

Section << 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>​

Section ​<< 09 9100 - Painting>>​

Section << 22 0529 - Hangers and Supports for Plumbing Piping and Equipment>>

Section << 22 0548.23 - Vibration and Seismic Controls for Mechanical Systems>>

Section << 22 0713 - Plumbing and HVAC Insulation>>

Section << 22 0813 - Testing Piping Systems>>

Section << 31 2000 - Earth Moving>>

Reference sTANDARDS

49 CFR 192 - Transportation Of Natural and Other Gas By Pipeline: Minimum Federal Safety Standards.

49 CFR 192.285 - Plastic Pipe: Qualifying Persons to Make Joints.

49 CFR 192.287 - Plastic Pipe: Inspection of Joints.

49 CFR 192.627 - Tapping pipelines under pressure.

49 CFR 192.629 - Purging of pipelines.

API 1104 - Welding of Pipelines and Related Facilities.

API Spec 5L - Line Pipe.

ASCE 7 - Minimum Design Loads and Associated Criteria for Buildings and Other Structures.

ASME B1.20.1 - Pipe Threads, General Purpose, Inch.

ASME B16.3 - Malleable Iron Threaded Fittings: Classes 150 and 300.

ASME B16.5 - Pipe Flanges and Flanged Fittings:  NPS 1/2 Through NPS 24 Metric/Inch Standard.

ASME B16.9 - Factory-Made Wrought Buttwelding Fittings.

ASME B16.11 - Forged Fittings, Socket-Welding and Threaded.

ASME B16.21 - Nonmetallic Flat Gaskets for Pipe Flanges.

ASME B16.40 - Manually Operated Thermoplastic Gas Shutoffs and Valves in Gas Distribution Systems.

ASME B18.2.1 - Square, Hex, Heavy Hex, and Askew Head Bolts and Hex, Heavy Hex, Hex Flange, Lobed Head, and Lag Screws (Inch Series).

ASME B18.2.2 - Nuts for General Applications: Machine Screw Nuts; and Hex, Square, Hex Flange, and Coupling Nuts (Inch Series).

ASME B31.8 - Gas Transmission and Distribution Piping Systems.

ASTM A53/A53M - Standard Specification for Pipe, Steel, Black and Hot-Dipped, Zinc-Coated, Welded and Seamless.

ASTM A105/A105M - Standard Specification for Carbon Steel Forgings for Piping Applications.

ASTM A106/A106M - Standard Specification for Seamless Carbon Steel Pipe for High-Temperature Service.

ASTM A234/A234M - Standard Specification for Piping Fittings of Wrought Carbon Steel and Alloy Steel for Moderate and High Temperature Service.

ASTM A269/A269M - Standard Specification for Seamless and Welded Austenitic Stainless Steel Tubing for General Service.

ASTM A307 - Standard Specification for Carbon Steel Bolts, Studs, and Threaded Rod 60 000 PSI Tensile Strength.

ASTM A563/A563M - Standard Specification for Carbon and Alloy Steel Nuts (Inch and Metric).

ASTM D2513 - Standard Specification for Polyethylene (PE) Gas Pressure Pipe, Tubing, and Fittings.

ASTM D3350 - Standard Specification for Polyethylene Plastics Pipe and Fittings Materials.

ASTM F436/F436M - Standard Specification for Hardened Steel Washers Inch and Metric Dimensions.

ASTM F1962 - Standard Guide for Use of Maxi-Horizontal Directional Drilling for Placement of Polyethylene Pipe or Conduit Under Obstacles, Including River Crossings.

ASTM F1973 - Standard Specification for Factory Assembled Anodeless Risers and Transition Fittings in Polyethylene (PE) and Polyamide 11 (PA11) and Polyamide 12 (PA12) Fuel Gas Distribution Systems.

ASTM F2620 - Standard Practice for Heat Fusion Joining of Polyethylene Pipe and Fittings.

MSS SP 97 - Integrally Reinforced Forged Branch Outlet Fittings: Socket Welding, Threaded, and Buttwelding Ends.

PPI - PE4710 - IPS and Large Diameter Metric HDPE Pipe Size Chart.

LANL-PERFORMED WORK

LANL Utilities and Infrastructure (UI) group will tie into existing gas piping system.

LANL UI will install regulator station and adjust outlet pressure of gas regulators.

      - ***************************************************************************************

      - Submittals shall be approved by the LANL UI gas system representative and the LANL Construction Inspector.

      - ***************************************************************************************

ACTION SUBMITTALS

Submit the following in accordance with Section << 01 3300 - Submittal Procedures>>:

Material, equipment, worker certifications and inspection reports:

Catalog data on regulators, pipe materials, pipe fittings, valves, pipe coating, pipe pig, accessories, directional drilling pull (weak link) device, special tooling (e.g., Lycofit fittings), and casing seals.

Certified Material Test Reports (CMTR) for metallic piping and components required by the code of record (e.g., <<ASTM A269/A269M>>).

Certificate of Compliance (CoC) to show compliance to the applicable codes and standards as identified in this S, specifically nonmetallic materials.

Per the requirements of Section(s) << 01 4444 - Offsite Welding, Brazing and Joining Requirements; and  01 4455 - Onsite Welding, Brazing and Joining Requirements>>, submit:

            - *************************************************************

            - For high risk applications such as ML-1 or ML-2, add submittals for “Weld Filler Material Control Procedures” and “Filler Material Certified Material Test Reports (CMTRs)” when required. Add “Post-Weld Heat Treatment Procedures” when required.

            - *************************************************************

            - *******Note: Only required as a submittal for Onsite welding, when subcontractor not using LANL WPS/PQR*******

Welding Procedure Specification (WPS) and supporting Procedure Qualification Record (PQR).

            - ********Note: Only required as a submittal for Onsite welding, when subcontractor not tested at LANL*******

Welder Performance Qualification Records (WPQR) including continuity.

Inspector qualification records

Inspection procedures

Weld inspection report(s) and weld map(s)

          - **********************************************************************

          - The following three subparagraphs are design choices.

          - **********************************************************************

Pipe pigging inspection report for 4-inch diameter and larger pipe and for all piping sizes with lengths greater than 500 feet.

Tracer wire catalog data. Installed with non-metallic pipe.

Tracing wire continuity test report.

Catalog data on identification tape.

Fabrication

Qualifications

Installer Qualifications

Documented OQ program per <<49 CFR 192.285>> Subpart “N” for all covered tasks

Special training required for mechanical fitting installation (e.g., Lycofit fittings).

Installation Instructions

Procedures

Prior to receiving materials submit the Material Control Procedure.

Before fabrication, submit the following procedures:

Code leak testing

Cleaning

Certified Factory Acceptance Test Report

Indicate codes under which all inspections and tests were conducted at the factory, include inspection and testing forms and logs.

Instrument Calibration Certificates for equipment used during the Factory Acceptance Test.

Field Test Reports

Field Test and Inspection Report providing evidence that the applicable code or standard was met.

          - **********************************************************************

          - Commissioning activities are the responsibility of LANL Utilities. The Constructor shall coordinate and provide all records necessary for LANL Utilities to complete the commissioning activities.

          - **********************************************************************

Commissioning (<<ASME B31.8>>, para. 841)

The following commissioning records shall be maintained as permanent records:

cleaning and drying procedures

cleaning and drying results

function-testing records of pipeline monitoring

control equipment systems

          - **********************************************************************

          - The following is a designer choice.

          - **********************************************************************

Submittals for the Horizontal Directional Drilling. Include calculations showing that proposed pipe can withstand all installation and in use stressors.

Certifications

Instrument Calibration Certificates for equipment used during the Factory Acceptance Test

QUALITY ASSURANCE

Clean and pig piping 4-inch diameter and larger, and all piping sizes with lengths greater than 500 feet.

WPS, WPQR, and Weld Inspection/Testing

Exterior Steel Pipe: <<API 1104>>

For pipe diameters up to 2.375 inches O.D., use LANL WPS API 1000-2

For pipe diameters greater than 2.375 inches O.D. and up to 12.75 inches O.D., use LANL WPS API 1000-1.

On-site and joining welding shall comply with LANL ESM Chapter 13 – Welding, Joining, & NDE; and Section << 01 4455 - Onsite Welding, Brazing and Joining Requirements>>.

Use LANL Welding Procedures

Welders shall be qualified at LANL by LANL

Off-site welding and joining shall comply with LANL ESM Chapter 13 – Welding, Joining, & NDE; and Section << 01 4444 - Offsite Welding, Brazing and Joining Requirements>>.

Weld Inspection: Weld inspection acceptance shall be in accordance with <<API 1104>>, Section 9, for steel pipe and LANL ESM Chapter 13 - Welding, Joining & NDE. Cracks shall not be accepted. Certified Weld Inspector (CWI) shall visually inspect 100 percent of the completed welds. Inspector should visually inspect base metal, filler metal, weld joint prep, temperature, and inter-pass temperature, weld fit up, root and subsequent passes when on-site.

Plastic Pipe: Comply with LANL ESM Chapter 13 - Welding, Joining & NDE and <<49 CFR 192.287>>.

LANL WPS to use for joining HDPE Performance Pipe:

| Pipe “A” Upstream | Pipe “B” Downstream |  |  |
| --- | --- | --- | --- |
|  | 8100 Yellow | 8300 Blk w/ Yellow stripes | 8400 Yellow w/ Blk stripes |
| 8100 | 7000-Gasx-PPE2 | 7000-Gasx-PPE2 | 7000-Gasx-PPE3 |
| 8300 | 7000-Gasx-PPE2 | 7000-Gasx-PPE3 (or PPE2) | 7000-Gasx-PPE3 |
| 8400 | 7000-Gasx-PPE3 | 7000-Gasx-PPE3 | 7000-Gasx-PPE3 |

          - Table Notes:

          - 8100 Driscopipe: The original, yellow outside/black inside, exists both as installed and limited stock on hand

          - 8300 Yellowstripe: Black with 4 yellow stripes, exists both as installed and limited stock on hand

          - 8400 BlackStripe: Yellow with 3 black stripes

          - On-site and joining welding shall comply with LANL ESM Chapter 13 – Welding, Joining, & NDE; and Section << 01 4455 - Onsite Welding, Brazing and Joining Requirements>>.

Use LANL Welding Procedures

Welders shall be qualified at LANL by LANL

Off-site welding and joining shall comply with LANL ESM Chapter 13 - Welding, Joining & NDE and Section << 01 4444 - Offsite Welding, Brazing and Joining Requirements>>.

Installation and inspection of each PE heat fusion joints, except for electrofusion, shall comply with <<ASTM F2620>>.

Electrofusion joints shall be made in accordance to user’s written procedures and the fitting manufacturer’s installation instructions.

        - ******************************************************************************

        - The following subparagraph is a designer choice.

        - ******************************************************************************

<<ASME B31.8>> Weld Inspection Requirements

Inspection of Welds on Piping Systems Intended to Operate at Hoop Stress Levels of Less Than 20 percent of the Specified Minimum Yield Strength:

The quality of welds shall be checked visually on a sampling basis, and defective welds shall be repaired or removed from the line.

Plastic pipe and tubing shall be carefully inspected for cuts, scratches, gouges, and other imperfections before use, and any pipe or tubing containing harmful imperfections shall be rejected. Each installation shall be field inspected to detect harmful imperfections. Any such imperfections found shall be eliminated.

If damage (e.g., scratches, gouges, etc.) exceeds 10 percent of the nominal wall thickness, then the pipe shall be replaced in its entirety

PART 2 - PRODUCTS

PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section << 01 2500 - Substitution Procedures>> except those item marked “No Substitution.”

Design requirements

Most widely or uniquely used at LANL applications are listed. The code of record is:

<<ASME B31.8>>

<<49 CFR 192>>

The design requirements for this system are as shown below:

        - ******************************************************************************

        - Total connected natural gas load in BTUs per hour, heat input requirement for each connected device in BTUs per hour, and pressure (psig) requirement at building wall. As part of the design, provide the total connected natural gas load in BTUs per hour, input requirement for each connected device in BTUs per hour with device room location, and pressure (IWC or PSIG) requirement at building wall.

        - Pipe shall be limited in design to less than 20 percent of SMYS.

        - Design pressure is 100 psig for wall thickness and testing.

        - Operating pressure is 60 psig for piping capacity.

        - Maximum actual operating pressure is 60 psig.

        - The total demand for each facility shall not be less than 100,000 BTU/hr.

        - ******************************************************************************

Design Pressure Distribution System: 100 psig

Design Temperature for buried pipe: 60 degrees F

Design temperatures for above ground pipe are

Winter: 5 degrees F dry bulb B.

Summer: 89 degrees F dry bulb, 60 degrees F wet bulb

Specified minimum yield strength (SMYS) of system: ​​​​​<< 19%; or  _______>>​​​​​

Class location unit: 4 (mandatory)

Total Demand for facility: ​​<< _______>>​​ BTU/Hr

Total Design Pressure for Facility ​​​​​<< 1;  2;  3;  4; and  _______>>​​​​​: ​​​​​<< XX psig or XX inches water column>>​​​​​.

Device ​​​<< 1;  2;  3;  4; and  _______>>​​​: ​​​<< Facilities and Room Locations>>​​​

Total Required Natural Gas << 5,000,000; or  _______>> BTU/Hr

SEISMIC PERFORMANCE REQUIREMENTS

      - ***************************************************************************************

      - The seismic exemptions noted below are based on ASCE 7-16. If the Code of Record for the project refers to a different version of ASCE 7, the Designer is responsible to check the seismic design requirements per that applicable edition.

      - ***************************************************************************************

Piping systems with trapeze assemblies/rod hangers that meet the requirements per <<ASCE 7>>, Section 13.6.7.3 are seismically exempt.

For piping systems not meeting the above exemptions, Structural EOR shall design seismic supports per ESM Chapter 5, Structural, Section II; <<ASCE 7>>, Chapter 13; and <<ASME B31.8>><< ; Section  01 8734 - Seismic Qualification of Nonstructural Components (IBC);  ; Section 22 0548.23 - Vibration and Seismic Controls for Mechanical Systems; or  None - N/A>> .

      - ***************************************************************************************

      - The following PART 2 Articles are designer choices based on project-specific requirements. Within each Article, paragraphs related to pipe material types, fitting types, component size ranges, etc. are designer choices based on project-specific requirements.

      - ***************************************************************************************

POLYETHYLENE PIPING, BELOW GRADE

      - ***************************************************************************************

      - Do not use polyethylene piping when design pressure exceeds gauge pressure of 100 psig (49 CFR 192.123). Provide 1-inch, 1-1/4 inch, 2-inch, or 3-inch PE service line and 2-inch-minimum PE main line as required for capacity and to integrate with the existing piping.

      - Provide calculations for performing Horizontal Directional Drilling (HDD) or other pipe pulling operations to ensure the piping will handle all stresses experienced during and after construction. Minimum SDR is SDR11 for HDD.

      - Use steel pipe if gas line is installed less than 20 feet from steam and condensate lines.

      - ***************************************************************************************

Manufacturer: Chevron-Phillips Performance Pipe (Driscopipe 8100 or Yellowstripe 8300 or Blackstripe 8400), No Substitution.

Pipe: Polyethylene, high density, <<ASTM D2513>>, <<PPI - PE4710>>, SDR 11 iron pipe size, <<ASTM D3350>> cell classification number 445574C.

Nominal Pipe Size: << 2;  3;  4;  5;  6;  8;  10;  12; and  _______>> inch

Fusion Fittings: Polyethylene, high density, butt heat fusion type, <<ASTM D2513>>, <<PPI - PE4710>>, SDR 11, <<ASTM D3350>> cell classification number 445574C.

Nominal Pipe Size Fittings: << 2;  3;  4;  5;  6;  8;  10;  12; and  _______>> inch

        - ******************************************************************************

        - Do not use electrofusion fittings without contacting a LANL UI gas system representative.

        - ******************************************************************************

Electro-Fusion Fittings: Polyethylene, high density, butt heat fusion type, <<ASTM D2513>>, <<PPI - PE4710>>, SDR 11, <<ASTM D3350>> cell classification number 445574C

Nominal Pipe Size Fittings: ​<< 2;  3;  4;  5;  6;  8;  10;  12; and  _______>>​ inch

Mechanical Fittings: Required for tie in to Drisco 8000-series HDPE piping, No Substitutions.

R.W. LYALL, LYCOFIT Coupling, <<ASTM D2513>>, <<PPI - PE4710>> (PE 3408), SDR11, iron pipe size 1 inch through 2 inch.

Nominal Pipe Size Fittings: ​​​​<< 1;  1-1/4;  1-1/2;  1-3/4;  2; and  _______>>​​​​ inch

Elster Permaset XL Coupling, <<ASTM D2513>>, <<PPI - PE4710>> (PE 3408), SDR11, iron pipe size 3 inch through 8 inch.

Nominal Pipe Size Fittings: ​​​<< 3;  4;  5;  6;  8; and  _______>>​​​ inch

STEEL PIPING, BELOW GRADE

      - ***************************************************************************************

      - Contact a LANL UI gas system representative for approval to use steel piping below grade. Provide minimum 2-inch steel service line.

      - ***************************************************************************************

Pipe: Black steel, <<ASTM A53/A53M>>, Type E, Grade B or <<API Spec 5L>>, EW, Grade B or <<ASTM A106/A106M>>, Grade B.

Nominal Pipe Size: << 1;  2;  3;  4;  5;  6;  8;  10;  12; and  _______>> inch

Schedule: ​<< 40;  80;  160;  standard; and  _______>>​

Fittings: Black steel, butt-welding type, <<ASME B16.9>>, <<ASTM A234/A234M>>, Grade WPB.

Nominal Pipe Size: << 1;  2;  3;  4;  5;  6;  8;  10;  12; and  _______>> inch

Fitting type: << elbow;  short radius elbow;  reducing elbow; and  _______>>

Wall thickness to match pipe schedule.

Coating: Factory applied fused system consisting of; an adhesive primer layer, with minimum 10 mil thermoplastic elastomer layer and minimum 40 mil polyolefin top layer containing UV protection; or alternate of an epoxy primer layer with minimum 50 mil high density polyethylene top layer; or an approved equal by the LANL UI Gas System Representative.

Manufacturers:

Tyco Adhesives, Synergy Plant Coating System

Tyco Adhesives, VANGUARD Plant Coating System

Product marking shall be in accordance with <<ASTM A53/A53M>>​, Section 21. Product marking shall be transferred to and stenciled to the outside of the pipe coating. Minimum transferred information shall include; pipe specification, grade, size, type, and heat number in accordance with the certified material test report and the product marking.

STEEL PIPING, ABOVE GRADE

Pipe: Black steel, <<ASTM A53/A53M>>, Type E, Grade B or API 5L EW, Grade B or <<ASTM A106/A106M>>, Grade B. Welded or flanged for pipe sizes above 2 inches, threaded for pipe sizes 2 inches or less.

Fittings 2 inches or less: Malleable iron, threaded type, <<ASME B16.3>>, Class 150

Nominal Pipe Size: << 1;  1-1/4;  1-1/2;  1-3/4;  2; and  _______>>​ inch

Fitting type: << elbow;  tee;  cross;  coupling; and  _______>>

Wall thickness to match pipe schedule.

Fittings greater than 2 inches: Standard wall, black steel, butt welding type, <<ASME B16.9>>, <<ASTM A234/A234M>>, Grade WPB.

Nominal Pipe Size: << 3;  4;  5;  6;  8;  10;  12; and  _______>> inch

Fitting type: << elbow;  short radius elbow;  reducing elbow; and  _______>>​

Flanges: Forged steel, <<ASTM A105/A105M>>, ANSI Class 150, weld neck, raised face, concentric serrations dimensions per <<ASME B16.5>>​.

Nominal Pipe Size: << 3;  4;  5;  6;  8;  10;  12; and  _______>>​ inch

Gasket <<ASME B16.21>>, Type “F”, 1/8 inch thickness, Gasket type: Flat Ring Material: Neoprene, durometer range A, hardness 50-65.

Nominal Pipe Size: << 3;  4;  5;  6;  8;  10;  12; and  _______>> inch

Flange bolts <<ASME B18.2.1>>, <<ASTM A307>> Grade B, UNC threads; hex nuts <<ASME B18.2.2>>, <<ASTM A563/A563M>> Grade A, UNC threads; and Type A plain washers <<ASME B18.2.1>> Hardened Plain Carbon Steel Washer (<<ASTM F436/F436M>> Washers), Bolt or stud number, diameter, and lengths as required by <<ASME B16.5>>, Class 150.

Machine Bolt, Stud Bolt diameter and thread: << _______>>​ inch UNC

Machine Bolt, Stud Bolt length: << _______>> inch

Bolt quantity: << 4;  8; or  _______>>

Nut Size and type: hex nut, inch UNC

Nut quantity: << 4;  8; or  _______>>

Washer size: Type A Series N plain carbon steel washer << _______>> inch

Washer quantity: << 4;  8; or  _______>>

PRESSURE REGULATOR STATION

      - ***************************************************************************************

      - Regulator stations are limited to the stations and regulators identified in the LANL Civil Standard DetailST-G3060-2. Specific regulator part numbers will need to be determined based on delivery requirements.

      - For parameters outside Civil Drawings ST-G3060-2, contact the ES-UI system engineer for regulator station design.

      - ***************************************************************************************

Regulator station and regulator shall meet LANL Civil Standard Detail ST-G3060-2 sheet ​​<< 1;  2;  3;  4; or  _______>>​​, No Substitutions.

LANL UI group will install and adjust outlet pressure of gas regulator station in conjunction with the subcontractor.

SHUT-OFF VALVE, ABOVE GRADE, THREADED ENDS, 1 & 2 inch

Manufacturer: Balon Series S, No Substitution.

Valve: Ductile iron body, threaded ends, non-lubricated full port opening ball valve, lever-operated, 1000 psig working pressure, size ​<< 1;  2; and  _______>>​ inch.

1 inch valve Part # 1F-S42-SE

2 inch valve Part # 2F-S42-SE

SHUT-OFF VALVE, ABOVE GRADE, FLANGED ENDS, 3 through 12 inch

Manufacturer: Balon Series F, No Substitution.

Steel body, flanged ends, non-lubricated full port opening ball valve, lever-operated, Class 150, size ​<< 2;  3;  4; and  _______>>​ inch. Balon Series F,  No Substitution

2 inch valve Part # 2F-F13-RF

3 inch valve Part # 3F- F13-RF

4 inch valve Part # 4F- F13-RF

Steel body, flanged ends, non-lubricated full port opening ball valve, gear-operated, Class 150, size ​​<< 6;  8; and  _______>>​​ inch. Balon Series F, No Substitution

6 inch valve Part # 6F-F13-RF

8 inch valve Part # 8F-F13-RF

Manufacturer: Balon Series T, No Substitution.

Steel body, flanged ends, non-lubricated full port opening ball valve, gear-operated, Class 150, size ​<< 10;  12; and  _______>>​ inch. Balon Series T,  No Substitution

10 inch valve Part # 10F-T13-RF

12 inch valve Part # 12F-T13-RF

SHUT-OFF VALVE, ABOVE AND BELOW GRADE, WELDED ENDS

Manufacturer: Balon US Series Weld X Weld,  No Substitution.

Valve: Steel body, butt welded ends, non-lubricated full port opening ball valve, Drive nut operated, Class 150, size << 2;  3;  4;  6; and  _______>>​ inch.

SHUT-OFF VALVE, BELOW GRADE, POLYETHYLENE

Manufacturer: Nordstrom Poly-Gas,  No Substitution.

Ball Valve for natural gas service <<ASME B16.40>>, <<ASTM D2513>>, material <<PPI - PE4710>> PPI-PE 4710 (PE 3408), for use with Performance Pipe (Driscopipe 8100 or Yellowstripe 8300 or BlackStripe 8400 designation), SDR11, iron pipe size 100 psig service pressure, butt fusion end connections.  Full bore when available.

Valve Size: << 1;  1-1/4;  2;  3;  4; and  _______>> inch

1 inch valve Part # 1-89111

1-1/4 inch valve Part # 1.25-89111

2 inch valve Part # 2-89111

3 inch valve Part # 3-89111

4 inch valve Part # 4-89111

ANODELESS RISER

Manufacturer: R.W. Lyall and Company, Inc.,  No Substitution

Prebent, 30-inch-radius minimum, <<ASTM F1973>>, <<ASTM D2513>>, <<PPI - PE4710>> (PE 3408), SDR11, iron pipe size NPT steel end by HDPE butt fusion, size to match piping system.  Steel pipe shall be standard wall, black steel, <<API Spec 5L>> EW, Grade A or <<ASTM A53/A53M>>, Type E, Grade A for 1 1/2 inch and less, Grade B for 2 inch and larger.  The mechanical joint shall be provided with a tamper proof, gas tight connection and seal per <<ASTM D2513>>, Category 1.

Required size:  << 1;  1-1/2;  2;  4;  5;  8; and  _______>>​ inch

TRANSITION FITTING

Manufacturer: R.W. Lyall and Company, Inc.,  No Substitution

Preformed steel pipe to HDPE pipe, <<ASTM D2513>>, <<PPI - PE4710>>​​ (PE 3408), SDR11, iron pipe size beveled steel end for welding by PE butt fusion, size to match piping system.  Steel pipe shall be standard wall, black steel, <<API Spec 5L>> EW, Grade A or <<ASTM A53/A53M>>, Type E, Grade A for 1 1/2 inch and less, Grade B for 2 inch through 8 inch.  The mechanical joint shall be provided with a tamper proof, gas tight connection and seal per <<ASTM D2513>>, Category 1.

Required size: << 2;  4;  6;  8; and  _______>> inch

Branch Connection

Manufacturer: Bonney Forge or approved alternative

<<MSS SP 97>>, or <<ASME B16.11>> paragraph 1.1.2 Special Fittings, Branch connection style is a Weldolet. Run to branch ratio must be 4:1 or greater. Material shall comply with <<ASTM A105/A105M>>.

Run pipe size:  << 4;  6;  8;  10; and  _______>> inch

Run pipe schedule:  << 40;  80;  160; and  _______>>

Branch Weldolet size:  << 1;  1-1/4;  2;  3;  4;  6; and  _______>>​ inch

Branch Weldolet schedule: << 40;  80;  160; and  _______>>

VALVE BOX

Manufacturer: Tyler, Series 6860

Valve Box: Cast iron, 5 1/4 inch shaft screw type, with lid marked GAS, length to suit burial depth.

Test lead stations

Below Grade Test Station

Manufacturer: C.P services, Glenn Test station, Non-locking lid

Above Grade Test Station

Rhino Tri-view Test Station 72 inches

TEST PLUG (PETE’s PLUG II or equal)

1/4 inch NPT, brass body, neoprene core, rated for 1,000 psig, complete with sealing cap and gasket, to receive 1/8 inch O.D. probe.

Pete’s Plug II Product Number 100

carrier pipe spacers and seal

GPT nonmetallic spacers model PE.

GPT Link-Seal® Modular seal- model “O”.

        - ******************************************************************************

        - Designer shall retain applicable pipe size(s).

        - ******************************************************************************

2 inches pipe and 4 inches carrier pipe - Link-Seal® LS-300-C with 6 links.

3 inches pipe and 5  carrier pipe - Link-Seal® LS-300-C with 8 links.

4 inches pipe and 6 inches carrier pipe - Link-Seal® LS-300-C with 10 links.

6 inches pipe and 10 inches carrier pipe - Link-Seal® LS-475-C with 10 links.

8 inches pipe and 12 inches carrier pipe - Link-Seal® LS-475-C with 12 links.

10 inches pipe and 14 inches carrier pipe - Link-Seal® LS-410-C with 15 links.

2 inches pipe and 16 inches carrier pipe - Link-Seal® LS-475-C with 17 links.

PART 3 - EXECUTION

preparation

Square and ream pipe ends and remove burrs.

Remove scale and dirt on inside and outside of piping before assembly.

Keep open ends of pipe free from scale and dirt.  Whenever work is suspended during construction, or at the end of each workday, protect open ends with temporary plugs or caps.

      - ***************************************************************************************

      - Butt weld ends shall meet ASME B31.8 Mandatory Appendix I, End Preparations For Buttwelding, including transitions. Joint details shall be provided in drawings or sketches issued by Engineer of Record.

      - ***************************************************************************************

GENERAL INSTALLATION

Furnish and install gas piping in accordance with <<ASME B31.8>> Gas Transmission and Distribution Piping Systems, and <<49 CFR 192>> Code of Federal Regulations.

Do not run gas piping below buildings, structures, or in crawl spaces.

Do not run gas piping under walks and equipment pads adjacent to building.  If unavoidable, sleeve line with non-metallic piping.

      - ***************************************************************************************

      - The following two paragraphs are designer choices.

      - ***************************************************************************************

Flange installation shall be in accordance with Section ​<< 01 4731 - Flange Assembly for Pressure Systems>>​.

Steel slip-on flanges, socket welds, and weldolets shall be welded to the dimensions provided in Section << 01 4631 - Welding, Brazing, and Soldering of Pressure Systems>>.

Paint outside gas regulator piping, valves, and appurtenances above ground. Gas piping color should be Forest Green and valves should be Slate Grey. Refer to Section << 09 9100 - Painting>>.

Support piping in accordance with Section << 22 0529 - Hangers and Supports for Plumbing Piping and Equipment>>.

Insulate piping system in accordance with Section << 22 0713 - Plumbing and HVAC Insulation>>. Provide clearance for installation of insulation and access to valves and fittings.

Minimum cover over pipe shall be measured from finish grade to top of pipe.

      - ***************************************************************************************

      - The following is a designer choice.

      - ***************************************************************************************

Butt weld ends shall be in accordance with <<ASME B31.8>> Mandatory Appendix I, End Preparations for Buttwelding.

Meet the requirements of <<49 CFR 192.627>> Tapping Pipelines Under Pressure, <<49 CFR 192.629>> Purging of Pipelines, <<ASME B31.8>> para. 841.2.7 Precautions to Avoid Explosions of Gas–Air Mixtures or Uncontrolled Fires During Construction Operations, and <<ASME B31.8>> para. 831.4.2 Special Requirements (j).

cleaning of natural gas piping interior

Use a pipeline pig to clean the interior of natural gas piping.  The pipeline pig used shall be of a type and configuration to provide optimum cleaning of scale, debris, and moisture from the pipeline interior.

Soft pigs shall be used with polyethylene pipe to avoid damage to the pipe.

A pressuring system shall be used to provide sufficient energy to drive the pig but to not overpressure the pipeline, the pressure to drive the pig shall not exceed the final test pressure.

A pig catcher of a design to provide a safe and effective means to receive the pig as it discharges from the line shall be used.

POLYETHYLENE PIPING INSTALLATION

      - ***************************************************************************************

      - Refer to LANL Civil Standard Detail ST-G30GEN-4 for trench width and piping burial depth.

      - ***************************************************************************************

Lay piping on trench bottom in such a manner as to snake piping from one side of trench to the other with one cycle approximately every 40 feet.  This will insure that sufficient piping material is available for expansion and contraction.

Provide minimum of 5 feet of cover over piping installed under any roadways and vehicle parking areas.  Minimum cover over pipe shall be from finish grade to top of pipe.

Perform butt heat-fusion joining in accordance with <<ASTM F2620>> and manufacturer’s written instructions. See PART 1, Quality Assurance article, including acceptable LANL Welding Procedures.

      - ***************************************************************************************

      - Refer to LANL Civil Standard Details ST-G30GEN-3 and ST-G30GEN-4 for trenching, piping burial depth, warning tape, and tracer wire details.

      - Refer to LANL ESM Chapter 3 - Civil, Section G30, for required minimum utility line clearances.

      - ***************************************************************************************

Refer to Drawings and Section << 31 2000 - Earth Moving>>, for earth cover, bedding, tracer wire, wire continuity test, warning tape, documenting new or exposed existing utility location, etc., requirements.

Make plastic-to-steel connection with transition fitting that is butt fused on plastic end and welded on steel end.

Mechanical fittings required for tie-in to Drisco 8000-series HDPE piping shall be installed as required by the fitting manufacturer using trained personnel, for example the Lycofit fittings and tooling.

      - ***************************************************************************************

      - Retain the following Article when horizontal directional drilling or cased boring required for project.

      - ***************************************************************************************

horizontal directional drilling or cased boring

Crossing of paved streets or roadways or other areas, (if approved by LANL UI Representative), will be accomplished by horizontal directional drilling (HDD) or cased boring, whenever practical. Casings for steel carrier pipe are not allowed. Care shall be exercised to ensure the paved surface is not damaged during the boring operation.

Directional Drill Bore Diameter: << 4;  6;  8;  10;  12; and  _______>>​ inch

Top of HDD or casing shall have a minimum burial depth of << 36;  60; and  _______>> inches.

Casing

Manufacturer:  Pittsburgh Pipe

Material: << ASTM A106/A106M; or  _______>>

Size:  << 4;  6;  8;  10;  12;  14; and  _______>>​ inch

When pulling in pipe the pulling force shall be monitored and kept below the Allowable Tensile Load (ATL) value of the pipe size and material per manufacturer’s recommendation. Both pipe ends shall be monitored for continuous, smooth movement. Pulling load from the equipment shall be monitored and the pipe lead end shall be equipped with a weak link device to disengage at the ATL or below. Manufacturer’s procedures and design parameters shall be followed, in addition to <<ASTM F1962>>.

The pipe shall be inserted into the casing in such a manner that the pipe and the casing insulators will not be damaged. Polyethylene pipe shall extend 3-5 percent of the pulled-in length past the termination points to allow for contraction. Polyethylene pipe shall be allowed 24 hours to recover from the pulling stress and contract to original pre-pull length and allowed to stabilize to buried soil temperature before final tie-ins are accomplished. A minimum of five (5) feet of pipe shall extend beyond the borehole or casing to allow for pipe damage assessment. Tracing wire shall be pulled in with the polyethylene pipe.

The annulus between the casing and the pipe shall be sealed with a waterproof mechanical seal, e.g., a Link-Seal.

Polyethylene pipe shall be allowed to snake in the casing and centering spacers are not required.

STEEL PIPING INSTALLATION

Butt weld underground steel piping.  See Quality Assurance in PART 1.

Use <<ASME B1.20.1>> threaded joints for above grade piping 2 inches and smaller and butt-welded or flanged joints for piping above 2 inches.

Apply Polyken primer 1019 or 1027 to underground joints, fittings, and valves, and spiral wrap with a double layer, half lapped, 35 mil tape, Polyken 934 system.  Follow manufacturer’s instructions.

Perform holiday test in accordance with the following procedure:

After pipe has been welded, joints wrapped, and pipe is ready for lowering into trench, test coating for flaws (holidays). Test coated piping system throughout its length for flaws in coating system by means of a high-potential flaw detector that can impress a maximum of 8,000 volts across coating.  One electrode of tester shall maintain complete circumferential contact with coating while transversing entire length of coating system and other electrode shall be the underlying metal pipe.  An electrical discharge through coating detected visually or by instrument, shall constitute failure of this test.

Actual working voltage of detector on pipe will depend upon thickness of coating and size of pipe. A thin coating on a large pipe will offer a capacitive load to the detector that will drop the working voltage several thousand volts below the "no-load" voltage. Detector output may also have to be increased to overcome conditions such as extremely dry rock, or sandy soil.

Important! Do not cut ground cable to a shorter length. The length supplied is important to proper operation of the detector. Keep as much of the cable as possible in contact with the earth. Straighten out kinks where possible and do not let it ride up over skids. In dry areas it will help to drag the cable in the ditch where there is more moisture. The pipe should be grounded.

Mark holidays as they are found and repair prior to lowering pipe into trench.  Repair holidays in factory coating by removing initial coating and undercoating for a minimum of 4 inches on each side of holiday.  Remove coating around holiday and feather edge to pipe wall for sufficient distance to make a satisfactory repair.  Apply primer (Polyken 1027) to the holiday to form a bond over the entire surface of the holiday and then spirally wrap pipe with a double layer of half-lapped 35 mil polyethylene tape (Polyken 934) for a minimum of 2 inches on each side of the holiday.

Repair holidays in joint wrappings by removing field applied coating in area of holiday and rewrapping. LANL STR or designated representative will approve all areas of joint coating.

      - ***************************************************************************************

      - Refer to LANL Civil Standard Details ST-G30GEN-3 and ST-G30GEN-4 for trenching, warning tape, and tracer wire details.

      - Refer to LANL ESM Chapter 3 - Civil, Section G30, for required minimum utility line clearances

      - ***************************************************************************************

Refer to Drawings and Section << 31 2000 - Earth Moving>>, for earth cover, bedding, tracer wire, wire continuity test, warning tape, documenting new or exposed existing utility location, etc., requirements.

Pressure testing

When pneumatically testing piping, the test area shall be cleared of unauthorized personnel due to contained energy. The area to be cleared for the pneumatic test shall be ​<< XXX feet per ASME PCC-2; or  XXX feet per (state other method)>>​.

All piping systems shall be tested after construction except for pre-tested fabricated assemblies and welded tie-in connections where post construction tie-in testing is not practical.

When all joints are accessible the soap bubble test will be used to locate leaks.

The circumferential welds associated with connecting pretested assemblies, pretested repair pipe lengths or sections, and welded tie-in connections not pressure tested after construction shall be inspected by radiographic or visual inspection with visual aids.

Nonwelded tie-in connections not pressure tested after construction shall be leak tested at not less than the pressure available when the tie-in is placed into service

Pressure test piping in accordance with Section << 22 0813 - Testing Piping Systems>> and as follows:

Sufficient time for joints to “set” properly or “cool” must be allowed before the test is initiated.

Do not test HDPE above 100 degrees F (38 degrees C).

Test with inert gas at 160 psig for not less than 1/2 hour for each 500 ft3 (14m3) of pipe volume or fraction thereof. Minimum duration of pressure test shall be 1 hour. The duration of the test shall not exceed 8 hours. Bring pressure to 160 psig and equalize to ambient temperature before starting pressure test; re-pressure as necessary to attain 160 psig prior to beginning test. Record test with calibrated testing equipment, calibrated and certified per LANL requirements prior to each pressure test. Recorded pressure line shall be continuous, even, and virtually “straight” without abrupt glitches, jogs or changes. The test pressure shall return to within five (5) percent of the starting position pressure at end of testing period. Do not use oxygen, acetylene, or other flammable/combustible gases or gas mixtures for leak testing.

Pressure test tie-in joints to existing system

Because it is sometimes necessary to divide a pipeline or main into sections for testing, and to install test heads, connecting piping, and other necessary appurtenances, it is not required that the tie-in sections of piping be tested.  The tie-in joints, however, shall be tested for leaks at line pressure.  The test procedure used, including the duration of the test, shall be capable of disclosing all leaks in the section being tested and shall be selected after giving due consideration to the volumetric content of the section and its location.  In this case, the soap bubble test will be used to locate leaks if the tie-in joint is accessible during the test.

piping TIE-IN

      - ***************************************************************************************

      - Refer to LANL Civil Standard Detail ST-G3060-1 for gas piping tie-in details.

      - If the natural gas distribution system requires a hot-tap operation, LANL UI qualified personnel shall perform the operation. A specific civil drawing will be issued for the installation. A specific list of the tools, materials, and PPE will be created for the operation. Either the manufacturer’s specific procedure covering the specific tooling and parts will be followed or LANL will create a specific procedure for the specific tooling and parts for the operation.

      - The requirements of 49 CFR 192.627 Tapping Pipelines Under Pressure, 49 CFR 192.629 Purging of Pipelines, ASME B31.8 para. 841.2.7 Precautions to Avoid Explosions of Gas–Air Mixtures or Uncontrolled Fires During Construction Operations, and ASME B31.8 para. 831.4.2 Special Requirements (j) will be met.

      - ***************************************************************************************

Tie-in to existing system will be performed by LANL UI.  Excavation, backfill, and materials required for tie-in shall be provided by Subcontractor.  Tie-in will be inspected by LANL STR and the LANL UI gas system representative.

LANL STR will notify LANL UI at least 15 working days in advance to schedule tie-in.

Before tie-ins are scheduled the LANL STR will ensure materials required for tie-in are on site, service lines have been tested, material submittals and all test reports have been approved by LANL UI and bell hole excavation meets access and OSHA requirements.

CORROSION CONTROL (STEEL PIPING BELOW GRADE)

      - ***************************************************************************************

      - Contact LANL UI Corrosion Specialist or the LANL UI Gas System Representative for cathodic protection requirements. Also refer to the LANL ESM Chapter 7 - Electrical, Section G4090.

      - ***************************************************************************************

<< _______>>

Repairs and retesting

Defective welds shall be repaired or removed

Weld repairs will be accomplished in accordance with <<49 CFR 192>>.245.

Indications of leakage are not acceptable. If leakage is observed during testing reduce pressure to zero, repair leak, and then complete pressure testing.

If leakage is observed during testing with flammable gas the repair will be in accordance with a written procedure to vent the system safely, make the line non-flammable if possible and, if not possible, what compensatory methods are needed, repair the leak, and then complete pressure testing.

Repair of non-standard mechanical joints shall be in accordance with a written procedure that vents the system to zero pressure, repairs the joint as defined by the manufacturer’s documentation, and then complete pressure testing.

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 33 5100, REV. 12, DATED APRIL 15, 2026.