Section 33 6300 
Steam Energy Distribution

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION SECTION

Rev. 6 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Civil POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable sections from all Divisions, especially Division 1, General Requirements.

      - Section is developed for ML-4 projects.  For ML-1, 2, and 3 applications, additional requirements and independent reviews should be added if increased confidence in procurement or execution is desired; see LANL ESM Chapter 1 - General, Section Z10 Specifications and Quality sections.

      - ==========================================================

      - Steam piping systems greater than 15 psig, upstream of the first steam shutoff valve (including systems and valves inside the building), shall comply with ASME B31.1, Power Piping.

      - Steam piping systems less than 15 psig shall comply with ASME B31.9, Building Services Piping; follow Section ​<< 23 2215 - Steam and Condensate Heating Piping and Specialties>>​. If serving a process in the scope of ASME B31.3 Process Piping, follow ​<< 40 0504 - Process Piping>>​.

      - For new buildings in TA-3:  When using the site steam distribution system, design for incoming temperature of 500 deg F and 125 psig; for the condensate return system, design for 250 degrees F and 125 psig.

      - For other pressure and temperature ratings, additional specification and restrictions may be required. Different products or materials are listed for each application.  Select one or any combination for the application.  Refer to Part 3 for valve and strainer installation instructions.

  - *************************************************************************************************************

PART 1 - GENERAL

SECTION INCLUDES

Site steam and condensate distribution piping, fittings, valves, steam trap, etc. See definitions below.

        - ******************************************************************************

        - The following subparagraphs are designer choices based on project-specific requirements.

        - ******************************************************************************

Steam Piping, Below Grade (150 psig maximum)

Condensate Piping, Below Grade (150 psig maximum)

Pre-Insulated Steam Piping, Below Grade (150 psig maximum)

Pre-Insulated Condensate Piping, Below Grade (150 psig maximum)

Steam Piping, Above Grade and in Steam Pits (150 psig maximum)

Condensate Piping, Above Grade and in Steam Pits (150 psig maximum)

Flanges, for Pipe Sizes Over 2 Inches

Small Steel Gate Valves (Threaded or Socket Weld Ends)

Large Steel Gate Valves (Flanged Ends)

Small Steel Globe Valves (Threaded Ends)

Large Steel Glove Valves (Flanged Ends)

Small Steel Check Valves (Threaded Ends)

Strainers (Threaded Ends)

Strainers (Flanged Ends)

Thermostatic Trap (Threaded Ends)

Expansion Joints

      - ***************************************************************************************

      - The following Section is not referenced in the body of this Section. Including it is a designer choice.

      - Section ​​<< 01 8113.13 - Sustainable Design>>​​

      - ***************************************************************************************

RELATED REQUIREMENTS

Section ​​​<< 01 2500 - Substitution Procedures>>​​​.

Section << 01 4000 - Quality Requirements - Non-Nuclear>>.

Section << 01 4115 - Pressure Safety Submittals>>.

Section ​<< 01 4444 - Offsite Welding, Brazing and Joining Requirements>>​.

Section << 01 4455 - Onsite Welding, Brazing and Joining Requirements>>.

Section << 01 4631 - Welding, Brazing, and Soldering of Pressure Systems>>.

Section << 01 4731 - Flange Assembly for Pressure Systems>>.

Section ​<< 01 8113.13 - Sustainable Design>>​

Section ​<< 01 8734 - Seismic Qualification of Nonstructural Components (IBC)>>​, for requirements pertaining to ​<< manufacturer’s certification; and  special certification>>​.

Section ​​​​<< 22 0529 - Hangers and Supports for Plumbing Piping and Equipment>>​​​​​.

Section << 22 0548.23 - Vibration and Seismic Controls for Mechanical Systems>> for << seismic-design criteria,; or  None - N/A>> submittal requirements, devices for seismic restraint, and installation requirements for these devices.

Section ​​​<< 22 0554 - Identification for Plumbing,  HVAC, and Fire Piping and Equipment>>​​​.

Section ​​​<< 22 0713 - Plumbing and HVAC Insulation>>​​​.

Section << 22 0813 - Testing Piping Systems>>.

Section ​​​<< 23 2500 - HVAC Water Treatment>>​​​.

Section << 31 2000 - Earth Moving>>.

REFERENCE STANDARDS

ASCE 7 - Minimum Design Loads and Associated Criteria for Buildings and Other Structures.

ASME B16.5 - Pipe Flanges and Flanged Fittings:  NPS 1/2 Through NPS 24 Metric/Inch Standard.

ASME B16.9 - Factory-Made Wrought Buttwelding Fittings.

ASME B16.11 - Forged Fittings, Socket-Welding and Threaded.

ASME B16.20 - Metallic Gaskets for Pipe Flanges.

ASME B31.1 - Power Piping.

ASME BPVC-IX - Boiler and Pressure Vessel Code, Section IX - Qualification Standard for Welding, Brazing, and Fusing Procedures; Welders; Brazers; and Welding, Brazing, and Fusing Operators.

ASTM A53/A53M - Standard Specification for Pipe, Steel, Black and Hot-Dipped, Zinc-Coated, Welded and Seamless.

ASTM A105/A105M - Standard Specification for Carbon Steel Forgings for Piping Applications.

ASTM A106/A106M - Standard Specification for Seamless Carbon Steel Pipe for High-Temperature Service.

ASTM A193/A193M - Standard Specification for Alloy-Steel and Stainless Steel Bolting for High Temperature or High Pressure Service and Other Special Purpose Applications.

ASTM A194/A194M - Standard Specification for Carbon Steel, Alloy Steel, and Stainless Steel Nuts for Bolts for High Pressure or High Temperature Service, or Both.

ASTM A216/A216M - Standard Specification for Steel Castings, Carbon, Suitable for Fusion Welding, for High-Temperature Service.

ASTM A234/A234M - Standard Specification for Piping Fittings of Wrought Carbon Steel and Alloy Steel for Moderate and High Temperature Service.

ASTM C591 - Standard Specification for Unfaced Preformed Rigid Cellular Polyisocyanurate Thermal Insulation.

LANL-PERFORMED WORK

LANL’s MSS Utilities Work Group will tie into existing site steam piping systems and condensate piping systems.

DEFINITIONS

      - ***************************************************************************************

      - For new buildings in TA-3 using the site steam distribution system, design for incoming temperature of 500 deg F and 125 psig. For the condensate return system design for 250 degrees F and 125 psig.

      - Piping shall enter the structure in a designated mechanical equipment room.

      - NOTE on LANL Ownership: Utilities normally owns steam piping up to and including the first shutoff valve inside the building (LANL ESM Chapter 1 - General, Section 200 designates this Opsystem USD – Utilities Steam Distribution, System STM – Steam). The building’s steam system (Opsys SD – Steam Distribution and Sys STM – Steam) is downstream of that valve. However, installation of these systems follows Sections << 33 6300 - Steam Energy Distribution>> and << 23 2215 - Steam and Condensate Heating Piping and Specialties>> (and thus ASME B31.1 and ASME B31.9 as appropriate, and without regard to ownership), so the ownership breakpoint is often different than the code/specification breakpoint.

      - ***************************************************************************************

For definitions and acronyms, refer to COE Glossary of Terms.

Steam Energy Distribution Piping: Steam piping upstream of the regulator outside the building.

Site Condensate Distribution Piping: Condensate piping downstream of condensate shutoff valve inside building, including steam trap piping upstream of first steam shutoff valve.

ACTION SUBMITTALS

      - ***************************************************************************************

      - Submittals shall be approved by the LANL UI Steam System Engineer.

      - ***************************************************************************************

Submit the following in accordance with Project submittal procedures:

Catalog data on pipe and pipe fittings, valves, steam traps, welding rod.

Certified material test report for the pipe.

Certification of welders and qualified welding procedures.

Welding Process Visual Examination Report.

Installation instructions for pre-insulated steam/condensate piping.

Plan and profile for steam/condensate piping system.

Thermal expansion calculation for steam/condensate piping system.

QUALITY ASSURANCE

Welding

Welders: Certified in accordance with <<ASME BPVC-IX>>.

Welding Materials and Procedures: Comply with <<ASME BPVC-IX>>​.

Visual Examination: Comply with <<ASME B31.1>>.

On-site welding shall comply with LANL ESM Chapter 13 - Welding, Joining & NDE and Section << 01 4455 - Onsite Welding, Brazing and Joining Requirements>>.

Off-site welding shall comply with LANL ESM Chapter 13 - Welding, Joining & NDE and Section << 01 4444 - Offsite Welding, Brazing and Joining Requirements>>.

        - ******************************************************************************

        - The following is a designer choice.

        - ******************************************************************************

Follow Section ​<< 01 4631 - Welding, Brazing, and Soldering of Pressure Systems>>​.

Dimensions

Dimensions (valves, fittings, and flanges): Comply with ASME B16 series standards.

Installation

Distribution Piping: Comply with <<ASME B31.1>>.

PART 2 - PRODUCTS

PRODUCT OPTIONS AND SUBSTITUTIONS

Alternate products may be accepted; follow Section ​​​<< 01 2500 - Substitution Procedures>>​​​.

SEISMIC PERFORMANCE REQUIREMENTS

      - ***************************************************************************************

      - The seismic exemptions noted below are based on ASCE 7-16. If the Code of Record for the project refers to a different version of ASCE 7, the Designer is responsible to check the seismic design requirements per that applicable edition.

      - ***************************************************************************************

Piping systems with trapeze assemblies/rod hangers that meet the requirements per <<ASCE 7>>, Section 13.6.7.3 are seismically exempt.

For piping systems not meeting the above exemptions, Structural EOR shall design seismic supports per ESM Chapter 5, Structural, Section II; <<ASCE 7>>, Chapter 13; and <<ASME B31.1>><< ; Section  01 8734 - Seismic Qualification of Nonstructural Components (IBC);  ; Section 22 0548.23 - Vibration and Seismic Controls for Mechanical Systems; or  None - N/A>> .

      - ***************************************************************************************

      - The following PART 2 Articles are designer choices based on project-specific conditions. Within each Article, paragraphs related to pipe material types, fitting types, component size ranges, etc. are designer choices based on project-specific requirements.

      - ***************************************************************************************

STEAM PIPING, BELOW GRADE (150 PSIG MAXIMUM)

Pipe: Black steel, <<ASTM A106/A106M>>, Grade B, Schedule 40.

Fittings (socket weld): Forged steel, <<ASTM A105/A105M>>, Class 3000, <<ASME B16.11>>.

Fittings (butt weld): Wrought carbon steel, <<ASTM A234/A234M>>, Grade WPB, Schedule 40, <<ASME B16.9>>.

Joints: Butt welded for pipe size 2 1/2 inches and larger and socket welded for 2 inches and below.

CONDENSATE PIPING, BELOW GRADE (150 PSIG MAXIMUM)

Pipe: Black steel, Schedule 80, <<ASTM A53/A53M>>, Type E or S, Grade B or <<ASTM A106/A106M>>, Grade B.

Fittings (socket weld): Forged steel, <<ASTM A105/A105M>>, Class 3000, <<ASME B16.11>>.

Fittings (butt weld): Wrought carbon steel, <<ASTM A234/A234M>>, Grade WPB, Schedule 80 <<ASME B16.9>> .

Joints: Butt welded for pipe size 2 1/2 inches and larger and socket welded for 2 inches and below.

pre-insulated STEAM PIPING, BELOW GRADE (150 PSIG MAXIMUM)

Manufacturer: Perma-Pipe, Multi-Therm 500, or Thermacor, Duo-Therm 505, factory prefabricated, pre-insulated piping system, suitable for 500 degrees F.

Distribution Pipe: Black steel, <<ASTM A106/A106M>>​, Grade B, Schedule 40.

Outer Conduit: Black steel, minimum 10 gage thickness.

Distribution Pipe Insulation: Mineral wool contained within a drainable, dryable, pressure tested steel conduit.

Outer Conduit Insulation: One-inch minimum polyurethane foam, <<ASTM C591>>, encased in fiberglass (FRP) jacket or high-density polyethylene (HDPE) jacket.

Pipe Fittings (socket weld): Forged steel, <<ASTM A105/A105M>>, Class 3000, <<ASME B16.11>>.

Pipe Fittings (butt weld): Wrought carbon steel, <<ASTM A234/A234M>>, Grade WPB, Schedule 40, <<ASME B16.9>>.

Joints: Butt welded for pipe size 2 1/2 inches and larger, and socket welded for 2 inches and below.

pre-insulated CONDENSATE PIPING, BELOW GRADE (150 PSIG MAXIMUM)

Manufacturer: Perma-Pipe, Poly-Therm, or Thermacor, Ferro-Therm, factory prefabricated, pre-insulated piping system.

Distribution Pipe: Black steel, Schedule 80, <<ASTM A53/A53M>>, Type E or S, Grade B or <<ASTM A106/A106M>>, Grade B.

Outer Conduit: Black steel, minimum 10 gage thickness.

Distribution Pipe Insulation: Mineral wool contained within a drainable, dryable, pressure tested steel conduit.

Outer Conduit Insulation: One-inch minimum Polyurethane foam, <<ASTM C591>>, encased in fiberglass (FRP) jacket or high-density polyethylene (HDPE) jacket.

Pipe Fittings (socket weld): Forged steel, <<ASTM A105/A105M>>, Class 3000 <<ASME B16.11>>.

Pipe Fittings (butt weld): Wrought carbon steel, <<ASTM A234/A234M>>, Grade WPB, Schedule 80, <<ASME B16.9>>.

Joints: Butt welded for pipe size 2 1/2 inches and larger, and socket welded for 2 inches and below.

STEAM PIPING, ABOVE GRADE AND IN STEAM PITS (150 PSIG MAXIMUM)

Pipe: Black steel, <<ASTM A106/A106M>>, Grade B, Schedule 40 (welded pipe).

Pipe: Black steel, <<ASTM A106/A106M>>, Grade B, Schedule 80 (threaded pipe).

Fittings (threaded): Forged steel, <<ASTM A105/A105M>>, Class 3000, <<ASME B16.11>> .

Fittings (socket weld): Forged steel, <<ASTM A105/A105M>>, Class 3000, <<ASME B16.11>>.

Fittings (butt weld): Steel, <<ASTM A234/A234M>>, Grade WPB, Schedule 40, <<ASME B16.9>>.

Joints: Threaded or socket welded for pipe sizes through 2 inches; butt welded or flanged for pipe sizes above 2 inch.

CONDENSATE PIPING, ABOVE GRADE AND IN STEAM PITS (150 PSIG MAXIMUM)

Pipe: Black steel, Schedule 80, <<ASTM A53/A53M>>, Type E or S, Grade B or <<ASTM A106/A106M>>, Grade B.

Fittings (threaded): Forged steel, <<ASTM A105/A105M>>, Class 2000 or 3000, <<ASME B16.11>>.

Fittings (socket weld): Forged steel, <<ASTM A105/A105M>>, Class 3000, <<ASME B16.11>>.

Fittings (butt weld): Steel, <<ASTM A234/A234M>>, Grade WPB, and Schedule 80, <<ASME B16.9>>.

Joints: Threaded or socket welded for pipe sizes through 2 inches, butt welded or flanged for pipe sizes above 2 inch.

FLANGES, FOR PIPE SIZES OVER 2 Inches

Flanges:

Forged steel, <<ASTM A105/A105M>>, ANSI Class 150, weld neck, raised face, dimensions per <<ASME B16.5>>​.

Gaskets:

Manufacturer: Flexitallic style CG; or Garlock style RW or Edge; or Lamons style WR.

Spiral wound metal with solid metal outer ring – winding metal of 304SS, filler of graphite, outer ring of carbon steel to <<ASME B16.20>> dimensions. Gasket thickness 0.175 inch and outer ring 1/8 inch thick.

Bolts, Nuts, and Studs:

Bolts/Studs: Alloy steel, <<ASTM A193/A193M>>​, Grade B7.

Nuts: Alloy steel, <<ASTM A194/A194M>>​, Grade 2H.

SMALL STEEL GATE VALVES (THREADED or SOCKET WELD ENDS)

Manufacturer: Vogt, Series 12111; or Velan, 2054B-02TY series.

Forged steel, <<ASTM A105/A105M>>​, Class 800, steam service, 500 degrees F at 1595 psig, conventional port, bolted bonnet, rising stem, threaded or socket weld ends, hard-faced seat and disc or 13% chrome disc and stem, Stellite 6 faced seat.

LARGE STEEL GATE VALVES (FLANGED ENDS)

Manufacturer: Velan, 0064C-02TY series.

Cast carbon steel, <<ASTM A216/A216M>>, Grade WCB, full port, bolted bonnet, Class 150, steam service, 500 degrees F at 170 psig, rising stem, flanged to <<ASME B16.5>> dimensions, 13% chrome faced disc, 13% chrome stem, Stellite 6 faced seat.

SMALL STEEL GLOBE VALVES (THREADED ENDS)

Manufacturer: Vogt, Series 12141; or Velan, 2014B-02TY

Forged steel, <<ASTM A105/A105M>>, Class 800, steam service, 500 degrees F at 1595 psig, conventional port, bolted bonnet, rising stem, threaded or socket weld ends, hard-faced seat and disc, or 13% chrome faced disc, 13% chrome stem, Stellite 6 faced seat.

LARGE STEEL GLOBE VALVES (FLANGED ENDS)

Manufacturer: Velan, 0014B-02TY

Cast carbon steel, <<ASTM A216/A216M>>, Grade WCB, bolted bonnet, Class 150, steam service, 500 degrees F at 170 psig, rising stem, flanged to B16.5 dimensions, 13% chrome faced disc, 13% chrome stem, Stellite 6 faced seat and disc.

SMALL STEEL CHECK VALVES (THREADED ENDS)

Manufacturer: Check-All CN or Durabla SCV with seal welded body

Spring-assisted, in-line, threaded, 316SS body, Inconel X-750 spring, cracking pressure of less than 0.25 psi, metal-to-metal seat, cold working pressure of at least 750 psig.

STRAINERS (THREADED ENDS)

Manufacturer: Keckley, SB-7.

“Y” Type, rated for 600 psig steam, 20 or higher gage mesh stainless steel screens, steel body, <<ASTM A216/A216M>>, grade WCB, with blowoff gate valve and plug.

STRAINERS (FLANGED ENDS)

Manufacturer: Keckley, SA-7.

“Y” Type, Class 150 psig, steam service, 20 or higher gage mesh stainless steel screens, steel body, <<ASTM A216/A216M>>, grade WCB, with blowoff gate valve and plug.

thermostatic trap (THREADED ENDS)

Manufacturer:

Yarway, 761-5 Bellows type.

Bestobell, GM16

Trap: Carbon or stainless-steel body, stainless steel trim, integral strainer, rated pressure of 300 psig at 650 degrees F.

Size, 3/4 inch or larger as determined by the LANL Steam System Engineer.

expansion Joints

      - ***************************************************************************************

      - Contact LANL Steam System Engineer for review and approval for use of appropriate expansion joint in piping system. Consult with manufacturer for part number.

      - ***************************************************************************************

Manufacturer: ADSCO Corruflex Equalizing series S11E10O.

Metal expansion joint, single controlled flexing bellows with ANSI flanged ends. 304 Stainless steel bellows.  Rated pressure and temperature 150 psig / 500 degrees F.

PART 3 - EXECUTION

PREPARATION

Ream pipe and tube ends. Remove burrs.

Remove scale and dirt on inside and outside of piping before assembly.

Keep open ends of pipe free from scale and dirt. Whenever work is suspended during construction, or at the end of each workday, protect open ends with temporary plugs or caps.

BURIED PIPING

      - ***************************************************************************************

      - Tracer wire and test stations are required when specifying cast iron, ductile iron, and non-metallic piping. Comply with LANL Civil Standard Details ST-G30GEN-3 for tracer wire/test station details and Civil Standard Drawing ST-G30GEN-4 for trenching detail.

      - Refer to LANL ESM Chapter 3 - Civil, Section G30, for required utility line clearances.

      - ***************************************************************************************

Refer to Drawings and Section << 31 2000 - Earth Moving>> for earth cover, bedding, tracer wire, wire continuity test, warning tape, documenting new or exposed existing utility location, etc., requirements.

INSTALLATION

Install in accordance with manufacturers’ instructions and <<ASME B31.1>>.

Route piping in orderly manner and maintain gradient.

Provide sleeve and packing gland or compressible modular seal between sleeve and pipes penetrating exterior walls or manholes below grade to provide a waterproof installation.

Install piping to allow for expansion and contraction without stressing pipe, joints, or connected equipment.

Provide clearance for installation of insulation and access to valves and fittings.

Slope steam and condensate piping 1 inch in 40 feet (0.25 percent) in direction of next low point.

Install valves with stems upright or horizontal, not inverted.

Use steel valves and strainers in piping above grade and in steam pits.

Provide eccentric reducers, flat on bottom, in horizontal runs of steam and condensate piping where line size changes.

Provide globe valves for throttling, bypass, or manual flow control services.

Provide gate valves for first steam valve inside building.

Connect steam and condensate branch lines into top of main or at a 45-degree angle from top of main.

Assemble welds per Article << 1.7; or  _______>>, Quality Assurance.

Assemble flanges per Section << 01 4731 - Flange Assembly for Pressure Systems>>.

Support piping per Section << 22 0529 - Hangers and Supports for Plumbing Piping and Equipment>>.

Pressure test piping per Section << 22 0813 - Testing Piping Systems>>.

Insulate piping per Section ​​​<< 22 0713 - Plumbing and HVAC Insulation>>​​​.

      - ***************************************************************************************

      - The following paragraph is a designer choice applicable to pre-insulated steam or condensate piping.

      - ***************************************************************************************

Install factory prefabricated, pre-insulated underground distribution piping per manufacturer’s instructions. Piping manufacturer shall provide factory trained field technical assistance for critical installation periods, e.g., field joint instructions and pressure testing.

Locate first steam shutoff valve inside building within 5 feet of building wall penetration.

Prior to operation: fill, clean, and chemically treat piping system. Refer to Section << 23 2500 - HVAC Water Treatment>>.

Label piping system per Section << 22 0554 - Identification for Plumbing,  HVAC, and Fire Piping and Equipment>>.

      - ***************************************************************************************

      - The following Article is a designer choice.

      - ***************************************************************************************

PIPING TIE-IN

      - ***************************************************************************************

      - Contact LANL Utilities and Infrastructure (UI) Steam System Engineer for point of tie-in and required details. Designer shall submit required details for specific installation to LANL UI Group for final approval. Refer to the LANL Civil Standard Detail ST-G3040-1 for tie-in detail.

      - ***************************************************************************************

Tie-in to existing steam and condensate piping systems will be performed by LANL’s Utilities Work Group.  Excavation, backfill, and materials required for tie-in shall be provided by Subcontractor.  The tie-in will be inspected by the LANL Subcontract Technical Representative (STR) and the LANL Steam System Engineer.

Notify LANL STR at least 15 working days in advance to schedule tie-in.  The LANL STR will notify LANL’s Utilities Work Group.

Prior to notifying Utilities Work Group, the LANL STR will ensure materials required for tie-in are on site, service lines have been tested, and material submittals and all test reports have been approved by LANL UI Group.

Pressure Testing

      - ***************************************************************************************

      - Special requirements exist for Boiler External Piping. Reference the B31 COR and the figures to determine applicability and requirements.

      - B31.1

        - Figure 100.1.2-1 Code Jurisdictional Limits for Piping — An Example of Forced-Flow Steam Generators with No Fixed Steam and Waterline

        - Figure 100.1.2-2 Code Jurisdictional Limits for Piping — An Example of Steam Separator Type Forced-Flow Steam Generators with No Fixed Steam and Waterline

        - Figure 100.1.2-3 Code Jurisdictional Limits for Piping — Drum-Type Boilers

        - Figure 100.1.2-4 Code Jurisdictional Limits for Piping — Isolable Economizers Located in Feedwater Piping and Isolable Superheaters in Main Steam Piping (Boiler Pressure Relief Valves, Blowoff, and Miscellaneous Piping for Boiler Proper Not Shown for Clarity)

      - When connecting to existing piping: Piping joints for ASME B31.1 pressure systems shall be leak tested in accordance with LANL ESM Chapter 17 - Pressure Safety, Section PS-REQUIREMENTS, 10.3 Pressure and Leak Testing.

      - ***************************************************************************************

Steam and Condensate Distribution Piping Systems (<<ASME B31.1>>)

Steam Distribution Piping: Test with water per <<ASME B31.1>>, para. 137 Pressure Testing.

Design Pressure ​​<< 125; or  ______>>​​ psig at ​​<< 500; or  ______>>​​​ degrees F.

<< Hydrostatic Test; or  Pneumatic Test>>.

Test Pressure ​​<< 188; or  ______>>​​ psig +/- ​​<< +5 - 0; or  ______>>​​ psig.

Test duration ​​​<< 10 minutes minimum;  ______; or  None - N/A>>​​​.

Condensate Distribution Piping: Test with water per <<ASME B31.1>>​, para. 137.

Design Pressure ​​<< 125; or  ______>>​​ psig at ​​<< 250; or  ______>>​​​ degrees F.

<< Hydrostatic Test; or  Pneumatic Test>>.

Test Pressure ​​​<< 188; or  ______>>​​​ psig +/- ​​​<< +5 - 0; or  ______>>​​​ psig.

Test duration ​​​<< 10 minutes minimum;  ______; or  None - N/A>>​​​.

      - ***************************************************************************************

      - The following two paragraphs are designer choices.

      - ***************************************************************************************

Pre-insulated Conduit Systems: Outer steel casing, test with air at 15 psig +/- ​<< _______; or  None - N/A>>​ psig for 1 hour or as otherwise specified in manufacture’s written instructions.

For modifications to existing piping, test the connection between new and existing at normal operating pressure. Bring system up to operating pressure gradually. Visually examine the piping for leaks at one-half the system operating pressure. Perform a final examination at the system operating pressure. No leaking from the piping indicates that the system meets the requirement of the project.

CORROSION CONTROL (only for Maintenance by LANL UI group)

      - ***************************************************************************************

      - Contact LANL UI Corrosion Specialist or the LANL UI Gas System Engineer for cathodic protection requirements.

      - NOTE: Pipe coating or cathodic protection is not required for factory pre-insulated piping systems (e.g., Perma-Pipe, Poly Therm).

      - ***************************************************************************************

Buried Pipe and Joint Coating: Field coating shall be a minimum of 30 mils thick and suitable for a continuous operating temperature of 250 degrees F.

Joints and Fittings: Apply a hand brush application of Polyken 1627 primer and a double layer of half-lapped tape, Polyken 1636, 30 mil.

Apply field coatings in accordance with the manufacturer’s instructions.

END OF SECTION

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

THE FOLLOWING STATEMENT IS FOR LANL USE ONLY

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 33 6300, REV. 6, DATED APRIL 15, 2026.