Section 43 3113.37 
High Efficiency Gas Purification Filters

  - *************************************************************************************************************

    - LANL MASTER SPECIFICATION section

Rev. 2 Summary of Changes: Edited and updated as required for import into SpecLink.

      - NOTE TO SPECIFIER ON USAGE IN SPECLINK: Activate the Section by turning on Seq #0000, followed by activating paragraphs in PART 1, Article SECTION INCLUDES. This will activate related articles, paras/subparas in the rest of the Section (i.e., PART 1 activates articles and paras/subparas in PARTS 2 and 3). If there are choice fields to edit the entire Section (typically in this first author note or beginning of the Section), make selections at those locations, which will filter through the remaining Section. All Articles, paragraphs and subparagraphs must be activated sequentially from top to bottom, unless noted otherwise.

      - This template must be edited for each project. In doing so, Specifier must add job-specific requirements. Selections and choice fields are used to indicate designer choices or locations where text must be supplied by the designer. The section must also be edited to remove requirements for processes, items, or designs that are not included in the project.

      - To seek a variance from applicable requirements in this Section, contact the Engineering Standards Manual (ESM) Mechanical POC  (LANL access only). Please contact POC with suggestions for improvement as well. LANL personnel should submit here: Suggested Change or Request Clarification; subcontractors via email to engstandards@lanl.gov.

      - When assembling a specification package, include applicable specifications from all Divisions, especially Division 1, General Requirements.

      - This specification section was prepared by an organization operating under a quality assurance program that meets the requirements of 10 CFR 830 (suitable for ML-1 through ML-4 projects).  Implementation of this specification requires modification to the specification to meet project-specific requirements.  Responsibility for application of this specification to meet project-specific requirements lies with the organization modifying or implementing the specification.  The organization modifying the specification shall apply a graded approach to quality assurance based on the management level designation of the project.  When this specification is used with nuclear facilities subject to 10 CFR 830, modification to this specification must be performed by an individual or organization operating under a quality assurance program that meets the requirements of that CFR.

      - ==========================================================

      - This Section serves as a template for procurement of filters at LANL.  There is a list of filters that are pre-approved for use in LANL.  The performance and design requirements for these filters can be found and referenced in the attachments.  If none of the pre-approved filters meet the performance or design requirements for a particular application, use this specification in its template format to procure a different filter.

  - *************************************************************************************************************

PART 1 - general

Section includes

High efficiency particulate filter used on gas piping systems.

This Section applies to filters for use in gas streams. When selecting filters ensure that the maximum temperature and pressure ratings of the filter and associated housing are within the particular system requirements.

This Section applies to the procurement of filters for Department of Energy (DOE) facilities at Los Alamos National Laboratory.

related requirements

Section << 01 2500 - Substitution Procedures>>

Section << 01 3300 - Submittal Procedures>>

Reference standards

10 CFR 830.122 - Nuclear Safety Management, Quality Assurance Criteria.

40 CFR 261 - Identification and Listing of Hazardous Waste.

ASME BPVC-V - Section V - Nondestructive Examination.

ASME NQA-1 - Quality Assurance Requirements for Nuclear Facility Applications.

ASTM A479/A479M - Standard Specification for Stainless Steel Bars and Shapes for Use in Boilers and Other Pressure Vessels.

ASTM B16/B16M - Standard Specification for Free-Cutting Brass Rod, Bar and Shapes for Use in Screw Machines.

ASTM E499/E499M - Standard Practice for Leaks Using the Mass Spectrometer Leak Detector in the Detector Probe Mode.

IEST-RP-CC013 - Calibration Procedures and Guidelines for Select Equipment Used in Testing Cleanrooms and Other Controlled Environments.

ISO 9001 - Quality Management Systems — Requirements.

Definitions

For definitions and acronyms, refer to COE Glossary of Terms.

Acceptance Test: Inspection and testing of a filter to verify certain characteristics or properties, which determine the acceptance or rejection of that filter.

Approved Test Aerosol: Particle-generating materials approved by DOE and used as test aerosols for performing testing of HEPA filters.

CMTR: Certified Material Test Report.

CoC: Certificate of Conformance.

EPA: Environmental Protection Agency.

High Efficiency Particulate Air (HEPA) Filter: A filter with a particle removal efficiency of at least 99.97 percent for 0.3 micrometer particles of an approved aerosol test.

IEST: Institute of Environmental Sciences and Technology.

Nominal Air Flow Rating: The flow rate which filters are identified by the manufacturer.

NPT: National Pipe Thread

Nuclear Facility: A DOE facility in which radioactive materials are produced or handled to the degree that environmental protection is required.

Penetration: The downstream test aerosol concentration, expressed as a percentage of the upstream test aerosol concentration.

PTFE: Polytetrafluoroethylene

QA: Quality Assurance

SST: Stainless steel

VCR: Swagelok’s trade name for metal gasket face seal fittings.

system description

Design Requirements

        - ******************************************************************************

        - Edit Design Requirements as necessary and add any additional criteria. Be sure to specify the following:

          - Filtration level

          - Housing operating pressure

          - Pressure differential at specified flow rate

          - Operating temperature range

          - Housing leak tightness

          - End fittings

          - Overall dimensions

        - The Attachments in this Section include filters commonly used at LANL and their specific specifications. If using a filter from the appendices, transfer data from attachment to the correct subparagraph or refer user to the appropriate attachment for design requirements.

        - Designer to retain either "Micron filtration..." or "Refer to Attachment(s)..." below. If the former is retained, retain all subparagraphs up to and including "Overall Dimensions...".

        - ******************************************************************************

Micron filtration: ​<< _______>>​ .

Housing to withstand a minimum pressure differential of ​<< _______>>​ in. of water or ​<< _______>>​ PSI.

Pressure differential of less than << ____>> in. of water or << _______>> PSI at a flow rate of << _______>> scfm.

Operating temperature range of << _______>> to << _______>> degrees F.

Leak Tightness of Housing: ​<< ____>>​.

End Connections: << _______>>.

Overall Dimensions: << ____>>.

        - *** all the above subparagraphs OR subparagraph below ***

Refer to Attachment(s) ​​​<< A;  B;  C; and  ______>>​​​.

Submittals

      - ***************************************************************************************

      - Submittal of QA plan is not necessary if filter manufacturer is on the current LANL Institutional Evaluated Suppliers List (IESL) (LANL access only) approved vendor list.

      - Consider requiring CMTRs for custom fabricated filter housings.

      - ***************************************************************************************

Submit the following in accordance with Section << 01 3300 - Submittal Procedures>>​:

Certificate of Conformance that is signed or otherwise authenticated by responsible managers within the supplying organization and that certifies the conformance of end-items to order requirements.  The Certificate of Conformance shall include:

          - **********************************************************************

          - The following two subparagraphs are designer choices.

          - **********************************************************************

Copy of the filter manufacturer’s QA plan identifying procurement, fabrication, test & inspection, material traceability and non-conformity controls for approval.

Certification that filters and filter housing have been designed manufactured and constructed in accordance with manufacturer’s QA plan and Article << 1.7; or  _______>> Quality Assurance and Testing.

Certification documentation showing that the filter meets the design requirements of Article << 1.5; or  _______>>  System Description, including material requirements of Article << 2.3; or  _______>>Materials of Construction. Examples of such documents include: supplier performance test information, inspection reports, justification for design integrity, drawings, etc.

Certification that any custom built filter housing was fabricated and leak tested to meet the requirements of this specification.  Examples of such document include: personnel certification for welding, inspection and leak testing, leak test procedures and reports.

Purchased item identified by model number.

Statement that the filter housing meets the leak test requirements in Article ​<< 1.5; or  _______>>​ System Description.

Purchase Order (PO) number.

Any approved changes, waivers, or deviations from this specification.

Installation Instructions.

Warranty documentation - guarantee against failure in proper use or operation caused by defective materials and/or workmanship for a period of 1 year from the date of acceptance.

quality assurance and testing

Seller’s Quality Assurance Requirements

Develop, implement, and maintain an approved QA system (including program/plan, procedures, and process control documents) in accordance with <<10 CFR 830.122>>.  If the seller’s QA plan is not in accordance with <<10 CFR 830.122>>, a LANL approved QA plan based on appropriate industry consensus standards, such as <<ISO 9001>> is acceptable.

Packaging and shipping

Package and ship filters per the requirements for level C items in accordance with <<ASME NQA-1>> and ship filters properly orientated, in accordance with manufacturer’s recommendation.

PART 2 - products

    - **********************************************************************************************

      - Consider filter environment when selecting acceptable materials.  Example: PTFE may not be an acceptable material for a radiation environment.  Also note, the listing of materials for filters is not a complete list of possible materials, others may be acceptable.  Again, carefully consider the environment (corrosion, radiation, etc) in which the filter will be operating.

    - **********************************************************************************************

manufacturers

The following is a list of some of the manufacturers with filters that may meet the requirements of this Section. However, these manufacturers are not exempt from any seller requirements including the submission of qualification certification for approval.

Mott Corporation.

Nuclear Filter Technology.

Pall Corporation.

PTI Technologies Inc.

Swagelok.

product options and substitutions

Alternate products may be accepted; follow Section ​​<< 01 2500 - Substitution Procedures>>​​.

Materials of construction

General

The following are not acceptable materials of construction:

Asbestos.

Cadmium-coated metals.

Any material that generates EPA regulated wastes as specified in <<40 CFR 261>>.

      - ***************************************************************************************

      - The Attachments in this Section include filters commonly used at LANL and their specific specifications. If using a filter from the attachments, refer user to attachment for additional materials of construction requirements.

      - Designer to retain either "Refer to Attachment(s)..." or "Filter Media..." below. If the latter is retained, retain all paragraphs up to and including "Gaskets and Seals."

      - ***************************************************************************************

Refer to Attachment(s) ​​​<< A;  B;  C; and  _______>>​​​ for Filter Media, Housing, End Fittings, and Gaskets and Seals.

      - *** paragraph above OR all the following paragraphs ***

Filter Media

Sintered metal, such as stainless steel, nickel and Hastelloy.

Ceramic.

PTFE.

Housing

Type 300 series stainless steel, conforming to <<ASTM A479/A479M>>​.

Brass, conforming to <<ASTM B16/B16M>>

End Fittings

End fittings shall be threaded or flanged.

Weld or solder fittings are not acceptable.

Gaskets and Seals

        - ******************************************************************************

        - The following subparagraphs are designer choices. Select at least one.

        - ******************************************************************************

Neoprene.

Metallic.

PTFE.

Viton.

Buna N.

Fabrication

      - ***************************************************************************************

      - Add additional fabrication requirements as necessary, such as welding.  Be sure to specify leak tightness and end connections for Filters.

      - ***************************************************************************************

General

Filters and housing

Fabricate in accordance with manufacturer’s approved QA plan.

Assemble Filter from materials designated in Article << 2.3; or  _______>> Materials of Construction.

Ensure that filter is free from foreign matter and damage.

Fabricate housing to << _______>> leak tightness.

Source Quality Control

Qualification and Acceptance Test Criteria

Perform factory design performance testing in the following categories:

Penetration – Test with DOE- approved aerosol and test method or the particle counter scanning method as described in <<IEST-RP-CC013>> .  If penetration of specified particle size exceeds << specify penetration>> penetration, filter is not acceptable.

Leak Testing – Perform helium leak test in accordance with <<ASTM E499/E499M>> or perform bubble leak testing in accordance with <<ASME BPVC-V>>, Article 10.

Perform factory product acceptance testing in the following categories:

Penetration – Test with DOE-approved aerosol and test method or the particle counter scanning method as described in <<IEST-RP-CC013>> .  If penetration of specified particle size exceeds << specify penetration>>, filter is not acceptable.

Resistance to airflow – The clean filter resistance to flow shall meet the requirements of Article System Description, paragraph << 1.5.A; or  _______>>​ Design Requirements.

Leak testing – Perform helium leak test in accordance with <<ASTM E499/E499M>> or perform bubble leak testing in accordance with <<ASME BPVC-V>> , Article 10.

PART 3 - execution

Examination

Inspect all filters upon shipment receipt and before installation for visual damage and compliance with specifications. Verify documentation from Article << 1.6; or  _______>> Submittals is included and is complete, and met specification requirements.

Storage

Store filters per the requirements for level C items in accordance with <<ASME NQA-1>>​ or in accordance with the manufacturer’s requirements, whichever is more restrictive.

installation

Install per manufacturer’s instructions.

Field Quality control

Notify Seller, Customer, ASM, and IQPA-IQ of filter rejections and re-evaluate the future procurement status of that manufacturer and/or model.

​<< END OF SECTION; or  END OF MAIN SECTION; ATTACHMENTS FOLLOW>>​

    - Attachment A: HEPA Filter – Nuclear Filter Technology High Efficiency, In-Line Filter Assembly

    - Attachment B: Filter – Swagelok, F Series, In-Line

    - Attachment C: Filter – Swagelok, TF Series, Tee type

    - **********************************************************************************************

      - Do not omit the following reference information:

    - **********************************************************************************************

The following Statement is for lanl use only

THIS PROJECT SPECIFICATION SECTION IS BASED ON LANL MASTER SPECIFICATION SECTION 43 3113.37, REV. 2, DATED APRIL 15, 2026.

    - attachment A

      - HEPA Filter – Nuclear Filter Technology High Efficiency, In-Line Filter Assembly

      - Design Requirements (Article System Description)

Particle removal efficiency of 99.97 percent of 0.3 micrometers or better of an approved test aerosol.

Pressure differential of less than 1.45 in. of water at 0.71 SCFM.

Helium leak tight (<1 x 10-6 cc/sec) housing.

End connections: 1/4 in. << NPT; or  VCR>> fittings.

Housing dimensions: 4 in. x 0.85 in. x 6.4 in., with fitting.

Materials (Article Materials of Construction)

Filter media – 316 SST, sintered metal.

Housing – 304 SST.

Gasket – N/A.

Fabrication (Article Fabrication)

No additional requirements

    - attachment B

      - Filter – Swagelok, F Series, In-Line

      - ***************************************************************************************

      - Pressure resistance and flow rate vary based on operating conditions. Consult manufacturer’s specifications.

      - ***************************************************************************************

      - Design Requirements (Article System Description)

0.5 micron filtration

Pressure differential of less than ​​<< _______>>​​ psi at ​​<< _______>>​​ scfm

Housing is not leak tight

Fitting size and end connection options:

1/8 in. Swagelok tube fitting

1/4 in. Swagelok tube fitting

3/8 in. Swagelok tube fitting

1/2 in. Swagelok tube fitting

3 mm Swagelok tube fitting

6 mm Swagelok tube fitting

​​​<< See manufacturer’s specification for more options>>​​​.

Housing dimensions: 9/16 - 1 in. dia. x 2.16 - 3.49 in. with fitting (varies by fittings)

Materials (Article Materials of Construction)

Filter media – 316 SST, sintered metal

Housing – 316 SST or brass

Gasket – silver plated 316 SST or aluminum

Fabrication (Article Fabrication)

No additional requirements

    - attachment C

      - Filter – Swagelok, TF Series, Tee type

      - ***************************************************************************************

      - Pressure resistance and flow rate vary based on operating conditions.  Consult manufacturer’s specifications.

      - ***************************************************************************************

      - Design Requirements (Article System Description)

0.5 micron filtration

Pressure differential of less than << _______>> psi at << _______>>​ scfm

Housing is not leak tight

Fitting size and end connections options:

1/8 in. Swagelok tube fitting

1/4 in. Swagelok tube fitting

3/8 in. Swagelok tube fitting

1/2 in. Swagelok tube fitting

6 mm Swagelok tube fitting

8 mm Swagelok tube fitting

​<< See manufacturer's specification for more options>>​

Housing dimensions: 9/16 - 1 in. dia. x 1.87 – 2.20 in.  x 2.13 - 3.04 in. with fitting (varies by fittings)

Materials (Article Materials of Construction)

Filter media – 316 SST, sintered metal

Housing – 316 SST or brass

Gasket – silver plated 316 SST or aluminum

Fabrication (Article Fabrication)

No additional requirements

END OF SECTION